Using Ultraviolet to Disinfect Household Drinking Water

How to construct and operate a small

ultraviolet water treatment system

Robert Catherman

Director of Safe Water Development

MEDRIX™

September 2007

Edition E.2.6

Edition E.2.6

Using Ultraviolet to
Disinfect Household
Drinking Water

How to construct and operate a small ultraviolet water treatment system

Robert Catherman

Director of Safe Water Development

MEDRIX™

September, 2007

Preface

The purpose of this handbook is to provide a standardized source of information for constructing and operating a Point-of-Use (POU) ultraviolet water treatment system.

This handbook includes:

- Part One: general understanding of the principles of ultraviolet water treatment.

- Part Two: instructions for the construction and assembly of an ultraviolet water treatment system.

- Part Three: instructions for operation and maintenance of the UV system.

- Part Four: methods of testing water quality.

- Part Five: methods of measuring and evaluating the performance of the equipment, its operators and its maintainers.

- Appendices: information and forms referenced in the main sections of the handbook.

MEDRIX declares the contents of this handbook to be open-source, available without charge. Copies of this handbook are available for downloading from the MEDRIX website.

Users assume full responsibility for the outcomes of constructing and operating water treatment equipment using these instructions.

MEDRIX’s intent is to translate this handbook into as many languages as proves useful. Formatting guidelines are available on the MEDRIX website.  www.medrix.org

A handbook edition number identifies the most up-to-date information. The letter before the edition number signifies the language of the document. The first number identifies the version; odd numbers indicate a version being drafted but not yet finalized; even numbers indicate a published and released version. The number following the period indicates the level of minor revision including corrections and updates. For example, the edition number “E.2.3” indicates this is the second English version released for publication with three levels of minor revisions. The edition number “V.2.2” indicates this is the Vietnamese translation of the English version E.2.2.

This handbook is designed to permit you, the user, to update pictures and information to reflect the realities in your part of the world. Feel free to substitute your own digital pictures to make the information more relevant to readers in your region. In some pictures in this handbook you may see pieces of equipment in the background that are not the same as the handbook describes. MEDRIX is constantly testing and adapting new ideas into the system and those ideas sometimes get into the pictures before they are ready to be formally documented. If the idea has value, works better than the current method and meets availability and cost criteria, you may see the new idea in the next edition of the handbook.

Your feedback about this handbook is welcome. Improving the quality of open source documents is the responsibility of all who use the information.

Submit suggestions and recommended changes for this handbook to:

Director of Safe Water Development

MEDRIX

PO Box 2588

Woodinville, WA 98072 USA

office@medrix.org

Include the edition number of this handbook in any communications.

This work is licensed under the Creative Commons Attribution-Share Alike 2.5 License. To view a copy of this license, visit http://creativecommons.org/licenses/by-sa/2.5/ or send a letter to Creative Commons, 543 Howard Street, 5th Floor, San Francisco, California, 94105, USA. You are free: to Share -- to copy, distribute, display, and perform the work to Remix -- to make derivative works Under the following conditions: Attribution. You must attribute the work to MEDRIX as the original creator and refer users to the MEDRIX website at www.medrix.org Share Alike. If you alter, transform, or build upon this work, you may distribute the resulting work only under a license identical to this one. For any reuse or distribution, you must make clear to others the license terms of this work. Any of these conditions can be waived if you get permission from the copyright holder.

Disclaimer

This publication is based on the collective experience of MEDRIX in monitoring and evaluating the equipment and procedures described herein. While every effort has been made to ensure the accuracy of this work, any judgments as to the suitability of information for the reader’s purposes are the reader’s responsibility. MEDRIX does not extend any warranties, and assumes no responsibility, for the suitability of this information or the consequences of its use.

The

Contents

Part 1: Ultraviolet Water Treatment for Producing Safe Water	1

Chapter 1: Introduction	3

Chapter 2: Understanding UV Water Treatment	4

Chapter 3: Testing Some Qualities of Water	8

Chapter 4: Deciding if UV Treatment is Appropriate for a Water Source	12

Part 2: Construction and Assembly of the UV Treatment System	19

Chapter 5: Locating Materials and Tools	21

Chapter 6: Constructing the Inflow Container and Optional Sand Filter	22

Chapter 7: Constructing the UV System Stand	31

Chapter 8: Constructing the UV Treatment Unit	41

Chapter 9: Constructing the Safe Water Storage Container	52

Chapter 10: Putting the System Together	56

Part 3: Operation and Maintenance of the UV Treatment System	61

Chapter 11: Starting the UV System after Setup	63

Chapter 12: Training the UV System Operators	66

Chapter 13: Daily Operation	68

Chapter 14: Regular System Maintenance	69

Part 4: Protocols for Testing Water Quality	71

Chapter 15: Testing Water for Microbiological Contaminants	73

Chapter 16: Testing Water for Turbidity	79

Chapter 17: Testing Water for Iron Content	83

Chapter 18: Testing Water for UV Transmissivity (UVT)	84

Part 5: Monitoring and Evaluation	87

Chapter 19: Reporting Water Quality Test Results	89

Chapter 20: Reporting Problems	91

Appendix A:  Forms	93

Form 1: Initial Assessment	95

Form 2: Follow-up Assessment	96

Form 3: Water Quality Test Results Log	97

Form 4: Water Quality Test Reporting	98

Form 5: UV Treatment System History Log	99

Form 6: Parts and Tools Inventory Form	100

Appendix B:  Parts Inventory	101

Appendix C:  Tool Inventory	118

Appendix D: The Science of Ultraviolet Energy and Water Treatment	132

Appendix E: Glossary of Terms	137

Appendix F:  Users Handbook	138

Appendix G:  UV Dosage Requirements	139

# Part 1:
Ultraviolet Water
Treatment for Producing
Safe Water

## Chapter 1:
Introduction

Safe Water for People in Need

According to the World Health Organization (WHO), 1.1 billion people around the world lack access to an improved source of water. Access to safe, clean drinking water is critical for proper health care, hygiene, sanitation, food production, education and economic activity. Safe drinking water is one of the foundational building blocks of individual lives, communities and nations..

In 2002 all member nations of the United Nations unanimously committed to work toward achieving the Millennium Development Goals (MDG). Goal number 7 of the MDG is to reduce by half the proportion of people without sustainable access to safe drinking water by 2015.

This goal is not attainable solely by building more community water supply networks. The time and resources required to implement these large-scale projects are too great.

In the recent years, household-level water treatment has emerged as a viable option for supplying large populations with an improved water supply in a short period of time. In 2003 the World Health Organization formed the International Network to Promote Safe Household Water Treatment and Storage. The Network’s mission is:

“To achieve a significant reduction in waterborne disease, especially among children and the poor, by promoting safe household water treatment and storage."

Several reliable methods are available for household-level treatment of water containing microbiological contaminants. Boiling is one effective and very common method currently used to produce safe water; but boiling also has some serious drawbacks,

MEDRIX has developed a simple, affordable treatment system using ultraviolet technology to inactivate most microbiological contaminants in drinking water. MEDRIX’s work has drawn on the earlier work of many others and particularly the work of Robert Rau of The Winfried Farmer Aid Fund.

This handbook describes how to construct and operate an ultraviolet water treatment system of appropriate size to meet the needs of a family, a small school or a rural health clinic.  Your feedback about this handbook is welcome. office@medrix.org

## Chapter 2:
Understanding
UV Water Treatment

This chapter includes:

- An explanation of ultraviolet radiation

- A description about how ultraviolet water treatment works

What is UV?

Ultraviolet (UV) energy is electromagnetic radiation. A low-pressure mercury vapor lamp resembling a fluorescent lamp produces UV radiation in the wavelength range of 254 nanometers (nm) commonly referred to as UV-C. This UV lamp is constructed using quartz glass that allows the UV-C radiation to pass through it; regular glass and plastic block all UV-C radiation. In this handbook, we will use the terms “UV radiation” and “UV energy” interchangeably.

UV-C radiation, or energy, is known to be an effective disinfectant due to its strong germicidal (inactivating) effect on many microbial contaminants. UV-C radiation is produced naturally by the sun but is filtered out by the earth’s atmosphere so that none reaches the earth’s surface. This filtering effect by the atmosphere is critical since UV-C is very damaging to the skin and eyes. Users should exercise extreme care to avoid exposure to skin and eyes when working with a UV-C germicidal lamp.

A brief history of UV

Ultraviolet radiation was first used for drinking water treatment in France in the early 1900s. However, early systems were abandoned due to high operating costs, unreliable equipment and the expanding popularity of disinfection by chlorine.

In more modern times, UV radiation is once again being used in some municipal water treatment plants in conjunction with other treatment methods such as filtration and chlorine sterilization. The popularity of ultraviolet treatment is increasing due to developing concerns regarding chlorine and its effects on human health as well as the ineffectiveness of chlorine in killing the protozoan parasite Cryptosporidium. Today, the use of UV energy to treat water for microbial contamination is an appropriate use of proven technology.

How does UV work?

UV radiation has three wavelength ranges: UV-A, UV-B, and UV-C. Only shortwave UV-C possesses germicidal properties capable of microbial inactivation.

UV-C radiation has a unique effect on microbial contaminants. The ultraviolet energy emitted by a UV-C germicidal lamp has the capacity to alter the nucleic acid (DNA) of viruses, bacteria, molds and parasites so they cannot reproduce and are thereby considered inactivated.

UV treatment does not alter the water chemically; nothing is added to the water as the UV-C energy passes through the water during treatment. However, it should be noted that inactivated micro-organisms are not removed from the water; they remain in the water, but in a state that allows them to harmlessly pass through the human body.

How does a UV water treatment system work?

In the UV water treatment system illustrated in Figure 1, gravity-fed water flows at a controlled rate under a UV-C germicidal lamp. The UV lamp is suspended above the water surface. The rate of water-flow is controlled to ensure the water receives an adequate  dosage of UV-C energy required to inactivate microbial contaminants.  These rates and dosages are based on scientifically-defined methods and accepted standards.

Figure 1: Air-suspended UV-C lamp inside reactor chamber

What is UV dosage and how is it measured?

Through research, biologists have determined the amount of UV-C radiation required to inactivate different kinds of microorganisms. The amount of UV radiation required is termed the dosage. The dosage is a function of the UV radiation intensity (expressed in power or microwatts) delivered for a given period of time (expressed in seconds) over a given area (expressed in square centimeters). A list of various microorganisms and the dosages required to inactivate them is found on Appendix G of this handbook.

A complete discussion of UV dosage and how it is calculated is found in Chapter 4 of this handbook.

Advantages of using UV radiation as a water treatment method

- The need to boil water is eliminated which saves time, reduces human energy requirements and conserves the environment.

- Fairly large quantities of water can be treated in a short period of time.

- No chemicals are added to the water.

Limitations of using UV radiation as a water treatment method

The most serious limitation to using UV-C energy in water treatment is that the treated water has no residual ability to inactivate new microbial contaminants introduced after disinfection has taken place. For comparison, chemicals such as chlorine have some ability to destroy new contaminates introduced into the water following treatment. It is important to protect water treated by UV-C radiation from the possibility of recontamination.

Furthermore, UV-C treatment does not remove dirt and particles, metals such as lead or iron, or hard minerals such as calcium from a water supply. In fact, many of these water variables may reduce the effectiveness of UV-C radiation on microorganisms.  Additional treatment may be required to remove particles, metals and minerals prior to passing water through a UV disinfection chamber.

The effectiveness of the UV treatment is influenced by several water quality factors:

- A low level of turbidity (cloudiness caused by suspended particles) is essential for successful treatment of water using ultraviolet radiation. Suspended particles in the water absorb UV energy or shadow microbes from the UV radiation. If turbidity is too high, some water may not receive the minimum UV-C dosage necessary to inactivate microbial contaminants, and the “treated” water may not be safe to drink. Chapter 3 discusses this problem and how to measure turbidity, and Chapter 6 describes how to use a sand filter to reduce turbidity.

- High concentrations of iron in a water source absorb UV energy, preventing the water from receiving the minimum UV-C dosage necessary to inactivate microbial contaminants. Chapter 3 discusses this problem and how to measure iron concentrations, and Chapter 6 describes how to use a sand filter to reduce iron levels in a water source.

- Dissolved substances in the water—especially organic carbon and nitrates—can also absorb UV energy. Chapter 3 discusses this problem and Chapter 18 discusses how to measure UV-C absorption caused by organic materials and nitrates.

Useful information about UV lamps

Not all UV lamps produce UV-C energy. Look for a label indicating a lamp is “germicidal” in order to confirm that it is designed to emit energy in the UV-C wavelength. However just because a lamp is labeled “germicidal” does not mean that it will produce an adequate amount of UV-C radiation for effective water treatment. If you are unfamiliar with a brand of lamp, measure the UV-C (254nm wavelength) output, i.e.- intensity, before using it for UV water treatment. Instructions describing how to use a radiometer to measure the output of a UV lamp are in Chapters 4 and 18.

The intensity of UV-C energy produced by a lamp may decline as the lamp ages. Most manufacturers recommend that lamps be replaced at least once every year. However, lamp output should be measured regularly, and lamps should be replaced when output falls below 80% of the original intensity when the lamp was new. Some UV-C lamp manufacturers advertise that lamps will last for 10,000 operating hours. However, some recent studies suggest that actual lamp life is closer to 4,000 or 5,000 hours.

The internet is an excellent source of more information on ultraviolet energy.

## Chapter 3:
Testing Some
Qualities of Water

This chapter includes:

- How water quality contaminants affect UV treatment options

- Testing for microbiological contamination, turbidity, iron, and UV transmissivity

First impressions

First impressions often set the tone for what is to follow. Let’s get a “first impression” of the water source you have to work with.

Put about 200 milliliters of source water in a clear container. Hold the container up to a light source. Is the water clear or does it have a definite “color”? Next, smell the source water. Does the water have any odor? Two or three people should examine the water and compare their observations. If the water has color or odor, then you have your first clues about the quality of the source water. Record your observations on Form 1-Initial Assessment in Appendix A.

Determining water quality and treatment options

Untreated water should be tested for the following properties before selecting ultraviolet treatment as an appropriate treatment method. These properties are:

- Presence of microbiological contaminants.  If microbiological contaminants are not present, then ultraviolet water treatment will have no effect on the water.

- Amount of turbidity. Pretreatment is necessary if the turbidity is too high.

- Amount of iron. If the iron level is too high, then pretreatment is necessary.

- Amount of UV transmissivity. Pretreatment is necessary if the UV transmissivity is too low.

A discussion of each of these properties follows.

Testing for Microbiological Contamination

Many serious diseases, such as diarrhea, typhoid fever and dysentery, can be traced directly to pathogenic microorganisms in contaminated water. These disease-producing organisms are found in fecal wastes and can be difficult to detect in water supplies.  This section shall only address tests for bacterial microorganisms.

Testing for specific bacterial pathogens can be impractical for many reasons. One important reason is the need for costly laboratory equipment and supplies as well as the requirement for complex test procedures. In an effort to overcome this obstacle, the generally accepted practice is to test for indicator bacteria instead of specific bacterial pathogens. These indicator organisms, usually not pathogenic, are present when pathogenic bacteria are present and absent when pathogenic bacteria are absent. Indicator bacteria are also usually of fecal origin, and if present in a water supply, can signify that fecal contamination has occurred.

A number of tests have been developed to detect fecal contamination of drinking water based on the presence or absence of various types of indicator bacteria. Although not as precise as testing for a specific organism, some of these fecal indicator tests are simple, low cost, and accepted as adequate alternatives when laboratory testing and bacteriological field test kits are unavailable or impractical. Prominent among these tests is the hydrogen sulfide, or H2S, test which detects hydrogen sulfide-producing bacteria in water supplies. H2S producing bacteria are considered to be strong indicators of fecal contamination, a relationship supported by their high correlation with the presence or absence of fecal matter.

Reminder:  The H2S test referenced here and discussed later in this handbook is only intended to indicate the presence or absence of a broad range of bacterial organisms that all produce H2S gas as a byproduct of their regeneration.  The significance and usefulness of this test rests in the general acceptance of its accuracy in indicating fecal contamination, low cost, ease of transport, and simple test procedures.

Detailed instructions on the H2S testing procedure are provided in Chapter 15.

Testing for Turbidity

Turbidity is the cloudiness or haziness of water caused by particles too small to be seen individually without magnification, much like smoke in air. While some suspended matter is large enough and heavy enough to settle to the bottom of a container if a water sample is left standing, small particles will settle slowly or not at all. These small solid particles cause a liquid to appear turbid. Measurement of turbidity is an important step in determining water quality.

A low level of turbidity is necessary for water to be successfully treated using ultraviolet radiation. The reason for this requirement is that suspended particles in the water will absorb UV radiation or cause shadows in the UV energy. If turbidity is too high, some microbial contaminants may not receive the minimum UV-C radiation dosage necessary to inactivate their ability to reproduce, and the “treated” water may not be safe to drink.

There are several practical ways of quantifying turbidity in water, the most direct being some measure of attenuation (reduction in strength) of light as it passes through a sample column of water. Electronic turbidity meters are available for precise testing, however, they are expensive. A turbidity tube is an alternative method of manual measurement, easily constructed, and provides an approximate measurement of turbidity which is accurate enough to meet our needs.

For detailed instructions on constructing a turbidity tube and testing for turbidity , see Chapter 16.

A commonly-used unit of measurement for turbidity is the Nephelometric Turbidity Unit or NTU.

- Untreated water must have a turbidity measurement of 5 NTUs or less prior to entering the UV-C disinfection chamber.

If the turbidity measurement is greater than 5 NTUs, turbidity can be reduced by first passing the water through a slow sand filter. (See Chapter 6)

Testing for Iron

It is common for ground water to pick up iron as it flows through soil formations. The presence of iron in water may produce an unpleasant metallic taste and vegetables cooked in iron-contaminated water turn dark. If the amount of iron in a water supply is above the World Health Organization (WHO) guideline of 0.3 mg/l, the water can cause staining of laundry or discoloration of faucets and basins. However, even high concentrations of iron are not considered a health problem. Even so, if water tastes bad, people may turn to other water sources, even those known to pose health hazards.

A high concentration of iron in the water increases absorption of UV energy causing some water not to receive the minimum UV-C dosage to inactivate microbial contaminants.

For detailed instructions about testing for iron, see Chapter 17.

If iron concentrations in the water are above 0.3 mg/l, one way to reduce the presence of iron is by passing the water through a slow sand filter (See Chapter 6).

Testing for UV Transmissivity

Transmissivity is defined as “the capacity of water to allow UV-C energy to pass through without absorption.”

As previously mentioned, the effectiveness of a UV-C disinfection system depends on the UV dose delivered to the water and the microorganisms in the water. The UV dose is determined from the combined effects of the UV energy intensity, the exposure time of the system and the UV Transmissivity (UVT) of the water.

If UVT of a water supply is too low, the UV energy emitted by the lamp will not efficiently penetrate the water, thereby reducing the UV-C dosage below acceptable standards.  Consequently, the resulting “treated” water may not be safe to drink.

UVT can be affected by various types of organic matter in the water. A common source of organic material is decaying plants. Sometimes organic material will “color” the water; however this is not always the case. UVT can not be determined by sight: it must be measured. The UVT of a water source can change with the weather and with the seasons.

UVT is further reduced by turbidity and iron in the water, as well as by some other less common chemicals.

For detailed instructions on measuring UVT, see Chapter 18.

Summary

Measurements of certain basic properties in a water source can determine if UV-C radiation may be used as an effective and appropriate treatment for microbial contamination. In the next chapter, you will read more about the step-by-step evaluation of a water supply and how to make important decisions concerning effective UV-C water treatment.

## Chapter 4:
Deciding if UV Treatment is Appropriate for a Water Source

This chapter includes:

- Explaining UV dosage

- Calculating UV dosage

- Evaluating effectiveness of UV treatment

- Determining correct flow rate for adequate UV treatment

Purpose

There are several effective methods of treating water contaminated by pathogens and each method has its own strengths and weaknesses.  This chapter will help you decide if UV radiation is an appropriate treatment method for a specific water source.

Important Information About This Chapter

It is not necessary to have a complete understanding of the science behind ultraviolet energy in order to use a UV-C Water Treatment System.  Such knowledge is helpful, but not a requirement.

This chapter contains some basic information on ultraviolet energy useful for operating and maintaining an effective UV-C Water Treatment System. If you are interested in supplementary information on the science behind UV energy, Appendix D contains a description of the theoretical basis underlying UV-C radiation as it relates to this handbook.  Reading Appendix D is optional.

However, it is necessary to follow the directions in this chapter in order to measure important characteristics of your water source and to decide if UV treatment will be effective in treating your water supply’s contaminants. If UV treatment is appropriate, then this chapter will help you determine the correct rate of water flow based on the four properties of a water source mentioned in the previous chapter.

Initial Assessment

Collect information using Form 1, Initial Assessment (Appendix A), during your first visit to a water source being considered for UV water treatment. The information you collect will help determine if UV-C radiation is an appropriate treatment method for that particular water supply

Calculating UV Dosage

The effectiveness of a UV disinfection system depends on the dose of UV-C energy delivered to the water. Appendix G summarizes the different UV dosages needed to inactivate various microorganisms. Because it is difficult to identify every microorganism present in a water source, it is also difficult to specify a minimum UV dosage requirement. A widely accepted international guideline is 30,000 µW-sec/cm2.  MEDRIX will use this value as a minimum-dosage requirement unless the country where this treatment system is used has a higher guideline.

UV dosage can be calculated using data from a radiometer designed to measure UV energy in the 254 nm (UV-C) range. Tool #2 in Appendix C is an example of this type of radiometer. The radiometer measures UV irradiance, or energy output, which is used to calculate UV dosage.

A modified UV disinfection chamber is required in order to safely and accurately measure UV-C irradiance. Details describing the construction and use of this modified chamber are contained in Chapter 18: Testing Water Samples for UV Transmissivity.  .

How to Measure UV-C irradiation for use in Calculating UV Dosage

- Turn on the UV lamp and allow it to warm up for two minutes.

- (Gloves must be worn during this step.) Without any water in the disinfection chamber, use a radiometer to measure the UV irradiance passing through the quartz monitoring window in the bottom of the chamber. The quartz window and chamber surfaces must be dry in order to get an accurate reading. Slowly adjust the position of the radiometer until you determine the highest repeatable irradiance reading. This measurement should be in the range of 800-1,000 μW / cm2.  Record this measurement on Form 1.

- Next, with the UV lamp still on, remove the cover from the chamber and fill the disinfection chamber with untreated source water to the level of the outlet baffle and replace the cover. Be careful to not expose your skin or eyes to UV-C energy.

- Once again, use the radiometer to determine the highest repeatable UV irradiance reading through the quartz monitoring window. (Gloves must still be worn for this step even though water is in the chamber.) This measurement should be in the range of 300-900 μW / cm2.  Record this measurement on Form 1.

- The irradiance value from Step 4 will be used to compute the maximum allowable flow rate later in this chapter.

Is Pretreatment Needed?

Obtaining a minimum dosage of UV-C radiation is critical to inactivating microbial pathogens and adequately disinfecting a water supply. As previously stated, high absorbance of UV energy by particles, metals, and organics in the water can cause UV treatment to be ineffective. Consequently, pre-treatment of a water supply to remove chemical or physical contaminants may raise the source water’s UV transmissivity to a level where UV disinfection can be effectively utilized.

Not all water sources require pre-treatment prior to being passed through a UV-C disinfection chamber.

Figure 1 on the following page will help you to decide if UV radiation will be effective treatment for raw source water or if some method of pretreatment will be required.

Figure 1: Deciding if UV Treatment is Appropriate for a Water Source

Answer the questions in the chart below using the turbidity, iron, and UV irradiance data from Form 1 that was taken from the water source during your initial assessment.

When Pretreatment of Source Water is Needed

If you answered "YES" one or more times in Figure 1, pretreatment of the source water is necessary before UV treatment can be successful. Read Chapter 6 on sand filters before deciding if UV radiation will be an effective method of treating this water.

When UV Radiation is Appropriate for Treating Raw Source Water

If you answered "NO" to all the questions in Figure 1, continue your evaluation by using Figure 2 on the following page to determine the maximum rate at which water should flow through the UV treatment system.

Determining the Maximum Flow Rate

The flow rate for water passing under the UV-C lamp is one of the principal calculations for determining the UV dosage delivered to a given water supply. Assuming that we are to meet the baseline dosage of 30,000 µW-sec/cm2, the upper line of Figure 2 shows the maximum flow rates allowable for your supply of source water as it passes under the UV lamp.  This flow rate is based on the UV irradiation measurement previously recorded in Step 4 (i.e.-while source water was present in the disinfection chamber) .

Safety Factor If you want to double the baseline UV dosage to 60,000 µW-sec/cm2 as a safety factor, the lower line in Figure 2 provides the maximum flow rates allowable for water passing beneath the UV-C lamp.

It is highly recommended that you begin operation of the UV Treatment System using the slower flow rates provided by the Safety Factor. Water that has spent extra time under the UV-C lamp will never be made less attractive to the user.  After evaluating the quality of treated water produced by the system over time, you may then decide to modify your system to allow for the faster flow rate based on the 30,000 µW-sec/cm2 minimum dosage requirement (upper line).

Figure 2: Determining the Maximum Flow Rate

Once you determine the Maximum Allowable Flow Rate, record this rate on Form 5- System History Log (Appendix A).

In Part 2 of this handbook, Chapters 5-10 describe construction and assembly of the UV Water Treatment System.

# Part 2:
Construction and
Assembly of the
UV Treatment
System

## Chapter 5:
Locating Materials and Tools

This chapter includes:

- Locating materials and tools

- Recording information for future use

Before construction can begin, you must locate the necessary materials and tools needed to assemble the UV water treatment system.  Here is some information to help you in this process.

1.	List of Materials and Tools At the beginning of each chapter is a list of materials and tools needed to complete each part of the UV system.

2.	Local Shops and Markets Look for local shop owners or market vendors who can provide the materials you need. To make your search easier, bring an actual sample or a picture of the materials or tools needed with you to the local shop or market.

3.	Explain Use to Seller Take time to explain to the seller how you will use the materials or tools. In some cases, when the seller understands the importance of the work you are doing, you will be able to purchase the materials at a lower price.

4.	Substitute Parts Many items will not be exactly the same as the pictures in this handbook. Your job is to find a substitute part to perform the same function. You may want to take digital photographs of the items you buy from local vendors and change the pictures in this handbook.

5.	Record Location Information When you locate a good source for an item, record where you purchased the item and its cost. Form 6, Parts and Materials Inventory Form, in Appendix A can be used to keep this record. Recording this information now will make your future work of locating materials and tools easier.

Good shopping!

## Chapter 6:
Constructing the Inflow Container and Optional Sand Filter

This chapter includes:

- Materials and tools needed to construct an inflow container

- How to assemble the inflow container

- How to prepare sand and pea gravel of correct size

- How to construct the sand filter

Purpose

Chapter 4 explains how to determine if your water source requires pre-treatment before you use the UV water treatment system. Review the results of the tests performed in Chapter 4 before continuing to read this chapter on constructing the inflow container as a part of the UV water treatment system.

If Pre-Treatment is Required

If pre-treatment is required, filtering the source water using a sand filter is a recommended option.

Sand Filters Sand filters are commonly used worldwide to reduce the level of contaminants in water. A sand filter has two functions in making UV treatment effective. The first function of a sand filter is to remove the particles in the water absorbing UV energy and limiting the UV energy’s ability to inactivate microbiological contaminants. The second function of the filter is to reduce iron content in the water. Iron also reduces microbiological contaminant inactivation by absorbing the UV energy. Sand filters are highly recommended because they have an added advantage of trapping potentially harmful cysts and eggs in water. Without the sand filter, these cysts and eggs might survive exposure to UV radiation. The sand filter will also remove some microbiological contaminants.

Limitations Sand filters have limits. Although sand filters can handle occasional turbidity up to 50 NTU without excessive clogging, the ideal input quality is much lower (less than 25 NTU) to minimize the need to frequently clean the sand filter. Water with greater turbidity (i.e., an NTU reading more than 50) will rapidly clog the filter. Let highly turbid water stand for several hours to allow particles to settle before pouring the source water into the sand filter.

If Pre-Treatment is Not Required

If the results of Chapter 4 indicate pre-treatment is not needed, continue with the construction instructions in this chapter, however do not put any sand in the inflow container.

Materials needed

| Part No | Description | Qty |
| --- | --- | --- |
| 6 | Container w lid, 20 liters | 1 |
| 7 | PVC 90 degree elbow with nut, 2.1 cm inside diameter (ID) of outlet opening | 1 |
| 7 | Rubber gaskets | 2 |
| 7 | 2.1 cm (7/8 inch) outside diameter (OD) PVC pipe, length - 5 cm | 2 |
| 8 | Valve | 1 |
| 9 | Flow restrictor (coin or flat plastic) | 1 |
| 12 | Filter pipe, 30 cm | 1 |
| 14 | Filter pipe end cap | 1 |
| 13 | Gasket for filter pipe | 1 |
| 16 | Label with operating instructions (waterproofed) | 1 |
| 17 | PVC pipe cement | 1 |
| 25 | Silicone sealant | 1 |
| 18* | Diffuser plate | 1 |
| * | Sand, properly sized, 10 kg | 15 |
| * | Pea gravel, properly sized, 10 kg | 4 |
| * | Wood for sieving frames |  |

* Required only if pre-treatment is necessary using sand filtering.

Tools needed

| Tool No | Description |
| --- | --- |
| 1 | Electric drill – 3/8 inch or larger |
| 6 | Tape measure with metric markings |
| 9 | 19 mm (3/4 inch) spade drill bit |
| 9 | 3.5 mm (9/64 inch) drill bit |
| 8 | Hacksaw |
| 3 | Matches or heat source to soften tubing |
| 10 | Knife |
| 20 | Watch or clock that can measure time in seconds |
| 21 | One liter measuring container |
| 11* | No. 18 sieve screen for sand |
| 12* | No. 45 sieve screen for sand |
| 13* | No. ???? sieve screen for pea gravel |
| 14* | Respirator mask |

* Required only if pre-treatment is necessary using sand filtering.

What container should you use?

The containers available in each part of the world differ greatly. The key is to find a container that is readily available at a reasonable price in your area. The containers should hold about 20 liters of water. The container should NOT have been used for storing hazardous materials such as gasoline or pesticides.

Carefully consider the appearance of the container and what a person will think when they see the system for the first time. The container should project an image of cleanliness that will reflect positively on the quality of the water being treated for drinking and other sanitary uses.

Assembling the inflow container

IMPORTANT: Read all of the following instructions BEFORE starting to work.

| 1 | Installing the outlet connection to the UV unit Choose a location to drill where the filter pipe will be correctly positioned (see steps 4 and 5). Use the 19 mm spade bit to drill a hole in the container’s corner near the bottom. The hole should be of correct diameter to allow the elbow fitting to be installed. Install the elbow fitting in the hole with one rubber washer on the inside and one on the outside. Tighten nut to prevent leaking. The exit elbow should be in a horizontal position. |  |
| --- | --- | --- |
| 2 | Constructing the flow restrictor Preferred Method: Select a coin to use for the flow restrictor. Its diameter should be slightly smaller than the 2.1 cm outside diameter (OD) PVC pipe. Optional Method: Select a piece of flat plastic for the flow restrictor. The piece should be thick enough so when a hole is drilled through it, the hole’s edges will be smooth and clean. Use a piece of PVC to draw a circle on the plastic the same diameter as the PVC. Cut out the circle and shape it so its diameter is slightly smaller than the PVC pipe. Determine the correct flow rate for treating your water source. Refer to Chapter 4 and the System History Log form. Determine how many 3.5 mm (9/64 inch) holes to drill according to the selected flow rate as shown below. Flow Rate Holes 3 L/min 3 2 L/min 2 1 L/min 1 Drill the correct number of holes near the center of the flow restrictor. Attach the flow restrictor into the end of a 5 cm piece of 2.1 cm outside diameter (OD) PVC using silicone sealant. Allow the sealant time to dry completely. Water must only flow through the holes you drilled in the flow restrictor. |  |
| 3 | Installing the flow restrictor Insert the flow restrictor glued to the end of the PVC into the outlet end of the valve. Do not cement this piece in place until you complete the flow rate check in Step 8. |  |
| 4 | Prepare the filter pipe Measure the diagonal dimension at the bottom of the container. See picture at right. Cut the filter pipe 12 mm shorter than the measured inside diagonal dimension. |  |
| 5 | Installing the filter pipe Slide the end cap on the end of the filter pipe. Place the 15 mm thick gasket around the nut on the elbow fitting inside the container. Place the filter pipe into the container and position the open end of the filter pipe against the gasket. Lower the filter pipe into a horizontal position. Check the gasket for an adequate seal to keep material from entering the filter pipe. |  |
| 6 | Installing the valve Connect the valve to the outlet elbow of the inflow container. Use a 5 cm piece of 2.1 cm outside diameter (OD) PVC. Cement the PVC and valve in place with the valve handle on top. The flow restrictor should be on the outlet side of the valve. |  |
| 7 | Checking for leaks Close the valve. Fill the container half full of water. Check for leaks. |
| 8 | Checking the flow rate Open the valve to full open position and use the one liter measuring container and a watch to measure the output flow rate. The flow rate should be no more than the maximum flow rate determined in Step 2. If the flow rate is greater than expected, go back to Step 2 and make sure the flow restrictor is installed correctly – water must not flow around the restrictor, only through the hole. |
| 9 | Adding the operating instructions Apply the operating instructions label to side of the container. The operating instructions are in Chapter 13. The instruction label should be waterproofed by laminating or by printing on adhesive-backed material. |  |

Optional Step – Setting up the sand filter

Preparing the sand and pea gravel

| 1 | Construct sieve frames Build three frames to hold the sieve screen. Each frame size should be approximately 25 by 25 cm. Attach sieve screen #18 (Tool 11) to one frame, sieve screen #45 (Tool 12) to the second frame and sieve screen #?? Tool 13 to the third frame. |  |
| --- | --- | --- |
| 2 | Removing large sand particles CAUTION: Wear a respirator mask to prevent breathing dust during sand screening. Put the sand onto the No 18 Sieve Screen. Save the sand passing through the screen for use in the next step. Discard the sand staying on the screen. This sand is too course. |
| 3 | Removing small sand particles Put sand from step 2 onto the No 45 Sieve Screen. Save the sand staying on the screen. Discard the sand passing through the screen. This sand is too fine. Perform this step with care. The fine silt and dirt must be removed before the UV system can be operated. It is much less work to remove the fine silt and dirt now by screening than later by washing. |
| 4 | Rinse the sand until the waste water is clear NEED SOME GOOD IDEAS– one idea is to put the sand in bags made from mosquito netting – each bag holds about 1 kg of sand. MEDRIX is testing this idea for practicality. |
| 5 | Pea gravel Sort about 5 kg of pea gravel. The size of each piece should be about the same size as a pea. It is OK if some pieces of gravel are 25% larger or smaller. |
| 6 | Adding the pea gravel, sand and diffuser plate Put the pea gravel inside the container. Add pea gravel until the filter pipe is covered. Put the sieved sand into the container on top of the pea gravel. The container should be about half full of sand and pea gravel. Put the diffuser plate inside the container on top of the sand. When water is poured into the container, the water should hit the diffuser plate and not go directly on the sand. |
| 7 | Flushing the sand filter Run water through the sand filter until the water coming from the outlet of the valve is clear |

## Chapter 7:
Constructing the
UV System Stand

This chapter includes:

- Materials and tools needed to construct the system stand

- How to measure and cut the pieces for the system stand

- How to assemble the system stand

Purpose

The system stand must be strong, stable and safe. The stand must support the weight of sand, water and equipment which can weigh as much as 40-45 kg (90-100 pounds). The system stand should not bend when the system is in operation. Extreme care must be taken to ensure a child or animal can not tip over the system.

The stand should also look nice, however appearance is always less important than safety. To make the stand more pleasing to the human eye, some PVC pipe can be successfully painted. Make sure the color chosen is consistent with the attitudes toward water in the culture where the water treatment system will be used.

Materials needed

| Part No | Description | Qty |
| --- | --- | --- |
| 17 | PVC Elbows, 21 mm (7/8 inch) inside diameter (ID) | 8 |
| 17 | PVC T’s, 21 mm (7/8 inch) inside diameter (ID) | 18 |
| 17 | 21 mm (7/8 inch) outside diameter (OD) PVC pipe, length in meters | 6 |
| 17 | Cement, PVC | 1 |
| 20 | Wood or Sheet Metal Screws, # 10 or 12, length 25-30 mm | 3 |
| -- | Paint (optional) |  |

Tools needed

| Tool No | Description |
| --- | --- |
| 6 | Tape measure |
| 18 | Marker pen |
| 5 | PVC cutter (optional – power saw) |
| 1 | Electric drill |
| 9 | Drill bit, 4 mm (5/32 in) |
| 7 | Screw driver |

Measuring and Cutting PVC Piping

| 1 | Measuring and cutting Measure and cut the PVC pipe in the following quantities and lengths. Write the part number on each PVC part. |  |
| --- | --- | --- |
|  | PVC Pipe Sections Stand Part Number Length, cm Quantity 1 13.5 6 2 17 6 3 not used not used 4 40 2 5 22.8 1 6 21.8 4 7 15 1 8 12 2 9 3.6 7 10 24 4 PVC Pipe Connectors Stand Part Number Quantity 17 - Elbows -- 8 17 - T’s -- 18 |

Figure 1: UV Water Treatment System Stand made of PVC piping

| 2 | Assemble the cross members Assemble three (3) cross member assemblies, each the same. DO NOT GLUE ANY PIECES TOGETHER UNTIL THE STAND HAS BEEN COMPLETELY ASSEMBLED |  |
| --- | --- | --- |
| 3 | Assemble the base Connect the T’s to the first cross member from Step 2. |  |
| 4 | Connect the lower shelf to the base Connect the second cross member from Step 2 to the base using T’s and part #10. |  |
| 5 | Add the left side upper legs and T-connectors Connect the two legs (part #4) to the lower shelf. Add T’s to top of each of the legs. |  |
| 6 | Assemble the right side upper legs and cross-bar |  |
| 7 | Add the right side upper legs and cross-bar |  |
| 8 | Assemble the top shelf Add elbows and connector part #9 to the third cross member from Step 2 to create the top shelf. |  |
| 9 | Connect the top shelf to the upper legs |  |
| 10 | Assemble the UV unit support |  |
| 11 | Connect the UV unit support to the stand |  |
| 12 | Assembling, adjusting and marking DO NOT CEMENT ANY PIECES TOGETHER AT THIS TIME. Assemble the stand on a level surface. Refer to Figure 1. Sometimes pieces of the same number are not cut exactly to the same length. If this is the case, you can overcome this problem by leveling the stand and marking the positions of the pieces at the joints before starting to cement. Use a level to adjust the connections at the joints so the stand is level both horizontally and vertically. |
| 13 | Test cementing Use scrap PVC pieces and elbows to test the cement’s hardening speed. You may be surprised how quickly the cement hardens. Practice until you become comfortable with the speed at which you must work when cementing the joints together. Joints can be taken apart after a few minutes but it takes an extreme amount of force. Try this by taking apart one of your test joints after allowing the cement to harden for a few minutes. |
| 14 | Cementing the pieces together Starting at the bottom, begin cementing the joints one at a time. There are many different ways to do this step – you will develop your own favorite method. Make sure that you can install the safe water storage container after the stand is assembled (see Step 2 in Chapter 10). If the container does not fit between the legs, you should not cement the top shelf to the upper legs; the top shelf should be removable so the safe water storage container can be easily removed for cleaning. At a few places, you may need to cement two joints at the same time. |
| 15 | Installing the leveling screws The purpose of the leveling screws is to provide a simple and easy method of leveling the UV treatment unit. Drill one hole in the center of one horizontal support PVC pipe supporting the UV unit. On the other side, drill two holes in the PVC pipe next to the elbow and T. Drill the holes entirely through both sides of the PVC pipe. Screw in the metal screws about one half their length. |  |
| 16 | Optional -- Paint the stand Spray paint the stand in a color that is associated with water in the culture where the stand will be used. In many cultures, blue is a good color for the stand. If available, special spray paint for plastics work best. |

An optional stand made from stainless steel is in development. The cost of metal makes this stand more expensive than the stand made from PVC but we have some ideas for reducing the price. A picture of this prototype stand is at the left.

## Chapter 8:
Constructing the
UV Treatment Unit

This chapter includes:

- Materials and tools needed to construct the UV treatment unit

- How to construct the UV treatment unit

- How to assemble the UV treatment unit

NOTE: Some minor but important modifications were made to the treatment unit design in August, 2007. The word “weir” was changed to “baffle” for simplified translation into other languages. The shape and position of the baffles were modified. The images and measurements in this chapter are the latest design; some images in other chapters still show the earlier design. Those earlier images will be changed in the next version of this handbook.

Purpose

The UV treatment unit is designed to expose water to ultraviolet (UV) energy to inactivate microbiological contaminants in the water.

This step is different from other steps in the construction process. Building the UV water treatment unit requires cutting, bending and welding sheet stainless steel. In most parts of the world there are skilled persons who can easily complete this step; the average person is not expected to have the tools and skills to complete this step. It will be necessary to find the right person to complete this step.

The price of the completed UV water treatment unit will depend on the cost of the materials, the profit expected by the metalworker and the volume of units produced. Good negotiating skills will help keep the price as low as possible.

The drawings and photographs included provide enough information for the metal worker to create a full-size pattern needed to cut out the pieces of stainless steel. As the system builder, you may want to create a model of the UV treatment unit from heavy paper or cardboard to demonstrate what the UV unit will look like when it is completed.

Germicidal UV lamps are available from major lamp manufactures such as Phillips, GE and Sankyo-Denki.

CAUTION: DO NOT TOUCH THE QUARTZ TUBE OF THE LAMP WITH YOUR FINGERS; HANDLE THE TUBE ONLY BY THE METAL AT THE ENDS

Bare skin contact with the quartz tube (“glass”) must be avoided. Compounds from the skin deposited on the lamps, when heated during operation, will form permanent etching on the quartz surface which will decrease UV energy transmission. A contaminated lamp will eventually overheat causing premature failure.

Figure 1

Materials needed

| Part No | Description | Qty |
| --- | --- | --- |
| 1 | 0.5 mm thick Type 304 stainless steel sheet metal approximately 50 cm by 75 cm | 1 |
| 2 | UV Germicidal Lamp, 8 watts, 30 cm – G8T5 | 1 |
| 3 | Lamp connectors (sometimes called “hangers” or “end caps”) | 2 |
| Tool 15 | Pop rivets | 4 |
| 4 | Ballast | 1 |
| 5 | Electrical power cord with 220 volt plug, length – 3 meters | 1 |
| 19 | Warning label about UV energy | 1 |
| 7 | Elbow fittings | 2 |
| 27 | Heat shrink tubing, wire nuts and electrical tape | 6 |
| 28 | Rubber grommets | 2 |
| 20 | Sheet metal screws for shield (# 10-12, 10 mm length) | 2 |
| 25 | Silicone sealant- |  |

Tools needed

| Tool No | Description |
| --- | --- |
| 15 | Pop rivet gun |
| 16 | Soldering iron and rosin-core solder |
| 7 | Screwdriver |
| 9 | Metal drill bits – various sizes ¼ + 5/32 + 1/8 pop rivets (3 mm + 4 mm + 7 mm) |
| 1 | Electric drill |
| 10 | Knife or wire stripper |
| 3 | Lighter |
| 9 | Bi-metal hole drill, 22 mm (7/8 in) |

UV treatment unit – plans for each piece

| 1 | Completed Reactor Chamber Exposed edges are rolled to prevent injury |  |
| --- | --- | --- |
| 2 | Reactor Chamber Top view |  |
| 3 | Reactor Chamber Side view |  |
| 4 | Reactor Chamber End view |  |
| 5 | Baffle Inlet end Baffle Outlet end |  |
| 6 | Completed Reflector Hood Exposed edges are rolled to prevent injury |  |
| 7 | Reflector hood Top view |  |
| 8 | Reflector hood End view Measure the width of the hood carefully. The hood must fit over the edges of the reactor chamber. |  |
| 9 | Ballast Cover This piece is made from a piece 20 cm by 20 cm and is bent as shown. |  |

Draw full-scale templates on paper for the parts from the dimensions shown.

Instructions for cutting, bending and welding this unit are beyond the scope of this handbook. However, important points learned from experience are included and should be passed on to the metalworker who will build this unit.

UV treatment unit construction

| 10 | Measuring and cutting the metal for the parts Use the templates for the parts to layout the stainless steel sheets for cutting. |
| --- | --- |
| 11 | Assembly Weld the seams, grind smooth and polish the exterior for a nice appearance. Polish the inside of reflector hood so it is highly reflective. This will increase the amount of UV energy delivered to the water. |  |

Installing the UV lamp and electrical components

| 12 | Marking and drilling holes in the reflector cover The locations and sizes of holes to drill depends on the shape, size and design of the lamp hangers and ballast used. Install the UV lamp hangers so the lamp is positioned as far as possible toward the exit end of the reflector chamber. Inspection hole (about 7 mm) is drilled at a location under the ballast shield and covered with a piece of transparent tape. See Step 6 for proper location. |  |
| --- | --- | --- |
| 13 | Installing lamp hangers Pop rivet the lamp hangers in place Test for correct fit by installing a lamp. DO NOT TOUCH THE QUARTZ TUBE OF THE LAMP WITH YOUR FINGERS; HANDLE ONLY BY THE METAL AT THE LAMP ENDS When finished, remove the lamp and store in a safe place. The sizes of lamp hangers vary which can cause a major problem. MAKE SURE THE LAMP WILL BE ABOVE THE WATER LEVEL when the system is operating. |  |
| 14 | Connecting the wires and ballast Rubber grommets, if available, should be used when electrical wires pass through a hole in metal to protect insulation on the wires. Insert rubber grommet in wire hole in reflector. The preferred methods of insulating the wiring connections are: heat shrink tubing, or wire nuts and electrical tape, or Electrical tape only. If heat shrink tubing is available, thread heat shrink tubing over the wires Connect the wires from the lamp hangers to the ballast following the wiring directions on the ballast Solder all wire connections Insulate the connections using heat shrink tubing, wire nuts and electrical tape or electrical tape only. Electrical tape loses its “stickiness” over time so apply an adequate amount of tape. Pop rivet the ballast in its place Connect and solder the power cord to the ballast wires Insulate the power connection using wire nuts and electrical tape or electrical tape only. |  |
| 15 | Installing the shield Attach the shield using sheet metal screws |  |
| 16 | Installing the power cord Insert rubber grommet in wire hole to protect insulation on wires Tie a knot in the power cord to provide strain relief. Pass the power cord through the grommet in the shield Connect the plug to the end of the power cord. |  |
| 17 | Attaching the warning label and water flow arrow Inspection hole. Attach the adhesive UV warning label facing up near the inspection hole At the inlet end, add an arrow showing the direction of flow of the water. This insures that the reflector hood is installed with the UV lamp positioned nearest the exit end of the chamber. The arrow in the photo is made from electrical tape but other materials can be used. |  |
| 18 | Testing lamp operation Test the system to be sure the UV lamp is working. CAUTION: Follow safe electrical practices. CAUTION: Do not look at the light from the UV lamp – UV rays can damage the eyes and burn the skin. |

Installing the fittings for water flow

| 19 | Marking and drilling inlet and outlet holes Mark the location to drill that will allow the nut on the elbow fitting to be easily installed. Use the bi-metal hole drill to drill an inlet hole in the UV unit trough. The hole should be of correct diameter to allow the elbow fitting to be installed. Follow the same procedure to drill the hole for the outlet elbow. |  |
| --- | --- | --- |
| 20 | Baffles Seal the edges where the baffle meets the bottom and the side walls of the chamber with silicone sealant to prevent leakage. |  |
| 21 | Installing the elbow fittings Install the elbow fitting in the inlet hole with rubber washers on the inside and outside. Tighten nut to prevent leaking. Tighten elbow in horizontal position. Follow the same procedure for the fitting in the outlet hole. |  |
| 22 | Testing for leaks Fill the UV unit trough with water. Check for leaks around the outlet baffle and at both elbows. |

## Chapter 9:
Constructing the
Safe Water Storage Container

This chapter includes:

- Materials and tools needed to construct the safe water storage container

- How to assemble the safe water storage container

Purpose

The safe water storage container is designed to store treated water until the water is used. After UV treatment, the water does not have any residual ability to inactivate microbiological contaminants introduced following treatment. Therefore, the storage container must be a “closed system”, as shown below in Figure 1, keeping stored water safe from contamination by hands, dippers or scoops.

The preferred option for safe water storage is to use a container specially designed for dispensing water as show in Figure 2. If a container like this is not available, you will need to construct a safe water container using locally available materials.

Figure 1								Figure 2

Materials needed

| Part No | Description | Qty |
| --- | --- | --- |
| 6 | Container w lid, 20 liters | 1 |
| 7 | Rubber gaskets | 2 |
| 7 | PVC 90 degree elbow with nut, 2.1 cm inside diameter (ID) of outlet opening | 1 |
| 23 | Spigot with rubber washers and nut | 1 |

Tools needed

| Tool No | Description |
| --- | --- |
| 1 | Electric drill |
| 9 | 19 mm (3/4 inch) spade bit |
| 9 | 15 mm (5/8 inch) spade bit |
| 6 | Tape measure |

Constructing the Safe Water Storage Container

| 1 | Installing the inlet connection from the UV container Read this entire step before deciding where to drill the hole for the inlet to the water storage container. Some containers are made from material that allows you to see how much water is inside the safe water container. If you can see the water level through the wall of the container, drill the hole in the top as show in the figure. OPTION: If you cannot see the water level through the container, you can make a simple change so you can know how much water is in the container. Instead of drilling the inlet hole near the top, drill the inlet hole near the bottom of the container. When assembling the system in Chapter 10, use a longer piece of clear tubing to connect the UV unit to the safe water container. The depth of the water in the container will be easily visible in the clear tubing. When the UV treatment unit is connected to the storage container, there should be no sharp bends in the tubing. Use a 19 mm spade bit to drill a hole in the container. The hole should be of correct diameter to allow the elbow fitting to be installed. Install the elbow fitting in the hole with rubber washers on the inside and outside. Tighten the nut to prevent leaking. Tighten the elbow and leave in a horizontal position. |  |
| --- | --- | --- |
| 2 | Installing the spigot Mark the position for the spigot before drilling the hole. The outlet of the spigot must be at least 1 cm above the bottom of the container. Drill a 15 mm (5/8 inch) hole for the spigot. Install the spigot in the hole with rubber washers on the inside and outside. Tighten the nut to prevent leaking. |  |
| 3 | Drill an air hole Drill a small hole near the top of the container to allow air to escape when the container fills with water. Choose a protected location for the hole so that nothing can enter the container to contaminate the treated water. |
| 4 | Checking for leaks Close the spigot. Fill the container half full of water. Check for leaks. |
| 5 | Option If you cannot find a spigot, you can make your own using the parts shown at the right. Use the same type elbow, washers, nut, valve and PVC tubing as used on other parts of the system. |  |

## Chapter 10:
Putting the System Together

This chapter includes:

- Materials and tools needed to assemble the entire system

- Directions for how to assemble the entire system

Purpose

After each part of the system is constructed, all the parts can be joined together to complete the assembling of the UV treatment system.

Materials needed

| Part No | Description | Qty |
| --- | --- | --- |
|  | Inflow container | 1 |
|  | System stand | 1 |
|  | Safe water storage container | 1 |
|  | UV treatment unit | 1 |
| 10 | 2.0 cm (3/4 inch) inside diameter (ID) clear tubing | 0.5 m |
| 17 | PVC cement |  |
| 17 | 2.1 cm (7/8 inch) outside diameter (OD) PVC pipe, length - 5 cm | 3 |

Tools needed

| Tool No | Description |
| --- | --- |
| 4 | Level |
| 7 | Screwdriver |
| 3 | Lighter |
| 10 | Knife |

Instructions for Putting the UV System Together

| 1 | Find the best location for the system Select a location where the system will be permanently located. The location you select must have an electric outlet within reach of the cord attached to the UV unit not be in a high traffic area such as a hall or walkway be as close as possible to the source of water being treated be safe from thieves and vandalism remain as clean as possible. Consider the presence of dust, mud, animal traffic, etc. in your choice of a location Once you have found a location, position the system stand so the extension arm is on your left when you face the stand. |
| --- | --- |
| 2 | Add the safe water container Put the safe water container on the lower shelf of the stand. |  |
| 3 | Add the UV treatment unit Put the UV treatment unit on the extension arm of the stand. Inside the UV unit, the baffle with the holes must be closest to the front. DO NOT CONNECT TO ELECTRICITY YET. |  |
| 4 | Level the UV unit Use the adjustment screws in the extension arm of the stand to level the UV unit in both directions. |  |
| 5 | Add the inflow container Put the inflow container on the top shelf of the stand. NOTE: Double check to be certain the correct flow rate restrictor is installed on the outflow side of the valve (see Chapter 6) |  |
| 6 | Connect the inflow container to the UV unit Insert a 5 cm piece of PVC into the elbow of the inlet to the UV unit. Measure and cut the correct length of tubing to connect the outlet of the valve to the inlet elbow of the UV unit. Remove the pieces of PVC from the elbow and the valve. Insert one piece of PVC into each end of the tubing. Soften the tubing by heating the end with matches or a lighter. Then slip the tubing over the PVC to form a water-tight seal. Connect the valve of the inflow container to the inlet of the UV unit using the tubing with the PVC in each end. If there are leaks at the connection points, then cement the PVC joints |  |
| 7 | Connect the UV unit to the safe water storage container Insert a 5 cm piece of PVC into the elbow of the outlet to the UV unit. Insert a 5 cm piece of PVC into the elbow of the inlet to the safe water container. Measure and cut the correct length of tubing to connect the outlet of the UV unit to the inlet elbow of the safe water container. Remove the pieces of PVC from the elbows. Insert one piece of PVC into each end of the tubing. Soften the tubing by heating the end with matches or a lighter. Then slip the tubing over the PVC to form a water-tight seal. Connect the outlet of the UV unit to the inlet of the safe water storage container using the tubing with the PVC in each end. |  |
| 8 | Update the System History Log Fill in the required information in Form 5, System History Log, found in Appendix A |
| 9 | Congratulations on reaching this milestone. Please email MEDRIX at office@medrix.org and tell us about your experience. MEDRIX wants to know where systems are operating worldwide to better understand how to reach the greatest number of people for the benefit of the improving the health of the global community. |

# Part 3:
Operation and
Maintenance of the
UV Treatment
System

## Chapter 11:
Starting the UV System
after Setup

This chapter includes:

- Materials and tools needed to begin operating the system

- How to process the first batch of water

Purpose

Before the first use of the system, some parts of the system must be sanitized to inactivate microbiological contaminants on the surfaces of the UV unit, tubing and safe water container. Remember, water treated by UV radiation has no residual ability to inactivate microbiological contaminants entering the water after treatment.

IMPORTANT: Any time the water treated by the UV system tests positive for microbiological contaminants,

- stop using the UV system for drinking water

- correct the problem and

- perform this sanitizing process.

Materials needed

Description

UV Treatment Unit

Safe Water Storage Container and connection tubing

Boiling water for sterilizing

Container to catch discarded water

Sanitizing and Starting the UV System after Setup

| 1 | Sanitize the storage container and connector tubing Disconnect the safe water storage container from the system. Keep the tubing from the UV unit connected to the safe water container. Boil about two liters of water for one minute. Close the spigot on the safe water container. Remove the top from the safe water container. Pour one liter of boiling water into the safe water container through the top. Replace the top on the safe water container. Shake the container so the water contacts all surfaces. Continue shaking for one minute Empty one half liter of water from the safe water container through the inlet tubing. Drain the remaining water from the safe water container through the spigot. |
| --- | --- |
| 2 | Sanitize the UV reactor unit Remove the cover from the UV unit. Disconnect the UV unit from the safe water container leaving the tubing connected to the UV unit Position a bucket to collect water coming from the outlet elbow. Boil about one liter of water for one minute. Pour one liter of boiling water into the outlet chamber of the UV reactor unit trying to keep the chamber full. Drain the water into a collection container through the outlet tubing. Discard the collected water. Replace the UV unit cover. |  |
| 3 | Reassemble the system Check the UV unit to be sure it is still level. Replace the cover on the UV unit. Replace the safe water container on the stand. Reconnect the tubing from the UV unit outlet to the safe water container. Close the spigot. |

Treating the first batch of water

Follow the instructions in Chapter 13 for operating the UV water treatment system.

Discard the first batch of treated water.

If the sand filter is installed, make sure the clarity of the water is acceptable.

Testing water quality for microbiological contamination

After the first batch of treated water is discarded, treat another batch and test the water quality.

Follow the instructions in Chapter 15 for testing the water for the presence of microbial contaminants after treatment by the UV system.

Materials needed

Description

UV Water Treatment System

Water Quality Test Kit

Water available to be treated

IMPORTANT: Do not drink water from the UV treatment system until the water quality test result is "negative" for microbiological contamination.

## Chapter 12:
Training the UV
System Operators

This chapter includes:

- Identifying who is responsible for training

- List of the topics for training

Purpose

Training is an important key to successful daily operation of the system. The water technician who sets up the UV treatment system is responsible for training the users to follow the correct procedures when operating the system. This training should be performed at the time the system is setup. The water technician is also responsible for training the user to test water for the presence or absence of microbial contamination.

Materials needed

Description

UV Water Treatment System

Water available to be treated

Container for water that will be discarded

Water Quality Test Kit

Form 3, Water Quality Test Results Log

User Handbook (see Appendix F)

Training the UV Water Treatment System Operators

| 1 | Preparing to train Complete the UV system setup steps in Chapter 11 Prepare a Users Handbook to leave with the trainees – see Appendix F Have water quality test supplies ready |
| --- | --- |
| 2 | Selecting persons to train One primary and one backup operator will be trained. Select persons who will be responsible for the daily water treatment. Arrange a training session when there is ample time to complete the training and when distractions are minimal. |
| 3 | Explain the UV system to the trainees Why is water treatment needed? How does the UV water treatment system work? . |
| 4 | Demonstrate how the system is operated correctly Use Chapter 13, Daily Operation, to train the operators |
| 5 | Ask the trainee to demonstrate correct system operation steps Have each trainee demonstrate how to operate the system Correct mistakes and misunderstandings Praise the trainees when they perform well |
| 6 | Demonstrate how to test water quality Use the instructions in Chapter 15 to train the operators to test water quality |
| 7 | Ask the trainee to demonstrate correct water testing steps Have each trainee demonstrate how to test a sample of water Instruct the trainee to record the test results on Form 3, Water Quality Test Results Correct mistakes and misunderstandings Praise the trainees when they perform well |
| 8 | Review Review the steps of the Daily Operation instructions Review the steps for water quality testing Remind the trainee to review the User Handbook whenever they have questions |
| 9 | Handling problems Inform the trainee regarding who to contact if they experience any problems. |
| 10 | Follow up Ask the trainees if they have any questions |

## Chapter 13:
Daily Operation

How to Operate the Ultraviolet Water Treatment System

Attach these instructions to the side of the inflow container.

STARTING:

- Close the valve and the spigot.

- Fill the inflow container. Use only water that looks clear. When adding water, do not pour the water directly onto the sand.

- Plug in the UV lamp and look for blue light in the inspection hole in the cover of the UV unit.

- Use the system ONLY if you can see the blue light in the inspection hole; indicating the UV lamp is operating.

- Wait for 2 minutes while the UV lamp warms up.

- Open the valve to begin treating water. Add more water as needed.

STOPPING:

- Check the blue light in the inspection hole to make sure the UV lamp is still operating. If the blue light is not “on” at this time, discard the water in the storage container and repair the system before using again.

- When the safe water container is full, close the valve, wait 2 minutes, then turn off the UV lamp.

- Loop the electrical cord from the UV unit over the valve handle to remind the next user to turn on the UV lamp before starting the water flow.

CAUTIONS:

- Always put treated water in a sanitized, clean container.

- Do not look at the light from the UV lamp – UV rays can damage the eyes and burn the skin.

- If the water output rate slows down significantly, it probably means the sand filter is becoming clogged.  Read the instructions about how to solve this problem.

## Chapter 14:
Regular System Maintenance

This chapter includes:

- Materials and tools needed to check the system for needed maintenance

- List of items to check

Purpose

All systems need periodic inspections to identify existing problems or potential trouble points. This maintenance inspection check and all necessary repairs should be performed by a certified technician.

Materials needed

| Part No | Description | Qty |
| --- | --- | --- |
| 2 | Digital Ultraviolet Radiometer | 1 |
| 15 | Water Quality Test Kit | 1 |
| Form 3 | Water Quality Test Results Log | 1 |
| Form 5 | The System History log | 1 |
| 20 | Watch | 1 |
| 21 | Measuring container marked in liters | 1 |
| See Ch 18 | UVT Test Reactor Chamber | 1 |

Inspection Points

- Review the periodic water quality test results recorded in Form 3, Water Quality Test Results Log

- Were the tests conducted at the specified time intervals?

- If the test was positive for bacteria, was appropriate action taken?

- If testing is not up-to-date, perform a water quality test.

- Review Form 5, the System History Log, looking for any problems and the date of last maintenance.

- Sanitize the system every other month following the instructions in Chapter 11. Record today’s date and the word “SANITIZED” on Form 3, Water Quality Test Results Log

- Quiz the operators about their knowledge of the system operation.

- Check the UV lamp output. Is the lamp output at least 900 µW/cm2 when measured through the quartz monitoring window with no water in the UVT test reactor chamber? If less than 900 µW/cm2, the lamp must be replaced.

- Measure UV energy transmittance (UVT) of the water being treated. Is the UV irradiance through the water measured using instructions from Chapter 4 less than 400 µW/cm2 which requires pretreatment of the water?

- Measure the water flow rate from the sand filter into the UV treatment unit.

- Is the flow rate correct for the water quality assessment of the untreated water? The correct flow rate is shown on Form 5, System History Log.

- Has there been any change in the quality of the untreated water source such as increased turbidity since the initial assessment? If yes, does the water quality need to be re-assessed?

- Is the sand filter clogged?

- Is the flow rate from the sand filter less than 1 liter per minute?

- Check physical condition and stability of equipment

- Is the system stable?

- Does the location of the equipment present any potential problems?

- Check electrical connections and safety

- Inspect wires for loose connections or breaks

- Does the plug connecting the cord to the electrical outlet fit tightly so it will not accidentally be disconnected?

- Ask the user if they ever receive a shock when touching the equipment.

- Are Operating Instructions posted on the system?

- Quiz some users about sanitation practices for use of treated water.

- Is there water on the floor under the system? This could indicate a leak in the system connections.

- Is the equipment dirty? If yes, ask user to cover the equipment with a cloth when it is not in operation.

Make a record of this maintenance inspection and the repairs made in Form 5, System History Log.

# Part 4:
Protocols for
Testing Water
Quality

## Chapter 15:
Testing Water for
Microbiological Contaminants

This chapter includes:

- Materials needed to test a water sample for bacterial contamination

- How to collect a water sample

- How to incubate the sample

- How to interpret and record the results of the test

- How to dispose of the sample

Materials needed

| Part No | Description | Qty |
| --- | --- | --- |
| 26 | Hand sanitizer | 1 |
| 15 | 20mL test bottles with caps | 1 |
| 15 | PathoScreen™ medium MPN pillows | 1 |
| 26 | Alcohol sanitizing swab | 1 |
| 15 | Bleach solution (5-6%) | 1 |

Tools needed

| Tool No | Description |
| --- | --- |
| 18 | Permanent marker |
| Form 3 | Water Quality Test Results Log |

Before you begin testing…..

If a reliable local organization is already responsible for monitoring water quality, consider using their testing services.

If testing services are not available or affordable, follow these instructions to conduct your own water quality test.

The Hach Company has give permission to reprint the PathoScreen Field Kit instruction manual (catalog number 28591-88). Information in italics has been added by the author of this handbook for the purpose of clarification and ease of translation into non-English languages. Some parts have been reformatted according to the guidelines for this handbook.

|  | ANALYTICAL PROCEDURE PathoScreen™ Field Kit |
| --- | --- |

Bacteria: Hydrogen Sulfide Producing -- Method 10032

Scope and Application: For detection of Salmonella, Citrobacter, Proteus, Edwardsiella, and some species of Klebsiella in drinking water, surface water, and recreational waters.

Media: PathoScreen* Medium Detecting Bacteria and Pathogens

Many serious diseases, such as typhoid fever and dysentery, can be traced directly to pathogenic microorganisms in polluted water. These disease-producing organisms are discharged in fecal wastes and are difficult to detect in water supplies. People may come in contact with these pathogens in drinking water or in recreational waters such as swimming pools, rivers, streams, lakes, and bathing beaches.

* PathoScreen is a trademark of Hach Company.

Direct testing for bacterial pathogens is often impractical and requires lengthy and complex test procedures, making the use of indicator organisms routine. Indicator organisms are usually of fecal origin. They are present when pathogens are present and absent when pathogens are absent. They are usually not pathogenic. No single organism satisfies all of the criteria for an indicator. For example, in temperate climates total coliform bacteria are commonly used as indicator organisms in potable water supplies. In most tropical climates indigenous E. coli produce positive reactions when traditional coliform tests are used. To minimize false positive results, other bacteria known to be associated with fecal contamination may be used as indicator organisms. Hydrogen sulfide-producing bacteria are associated with the presence of fecal contamination and may be used as indicator organisms.

The PathoScreen™ Medium detects the presence of hydrogen sulfide-producing bacteria including Salmonella, Citrobacter, Proteus, Edwardsiella, and some species of Klebsiella. Indigenous E. coli does not interfere with the PathoScreen test, which makes it an excellent alternative to coliform testing. The sterilized powder medium is easy to use and produces easy-to-interpret, reliable results. PathoScreen Medium is well-suited for monitoring drinking water systems in developing tropical countries, in remote field locations, and in disaster or emergency situations.

Preparing Sample Containers

Sample bottles must be sterilized before every use. Clean bottles thoroughly with soap and water, then perform the sterilization procedure. Wash hands thoroughly with soap and water to minimize contamination of sample.

Sterilization Procedure

| 1 | Add 10–12 drops of bleach solution to the bottle. Screw the cap on the test bottle. |  |
| --- | --- | --- |
| 2 | Swirl and invert the bottle to completely coat the walls of the bottle and inner surface of the cap. Allow the bottle to sit for 2 minutes. |  |
| 3 | Pour out the bleach solution. Do not pour the bleach solution into the water source to be tested. Replace the cap on the bottle. The bottle is now ready for use in the test. |  |

Conducting the Presence-Absence Test with PathoScreen Medium

Note: Wash hands thoroughly with soap and water to minimize contamination of sample.

| 4 | Label the sample test bottle with: Name of test location Water source (well, pipe, stream, etc.) Date and time of test Name of tester |  |
| --- | --- | --- |
| 5 | Use hand sanitizer on the hands of the testers, particularly on the ends of the fingers and under fingernails |  |
| 6 | Remove the cap from the bottle. Rinse the bottle several times with sample water. Fill the sterilized bottle to the shoulder with sample (approximately 20 mL). |  |
| 7 | Add the contents of one PathoScreen Medium powder pillow to the water sample. Note: To avoid contamination, swab the area of the tear on the pillow with an alcohol swab before tearing the pillow opening. |  |
| 8 | Screw the cap on the bottle immediately. Invert the bottle to thoroughly mix the water sample with medium. The color of the sample at this time should be yellow. |  |
| 9 | Place the bottle in a location with constant temperature at 25–35 °C (77–95 °F) for 24 to 48 hours. In many tropical locations, incubation in open air will meet these criteria. If the air temperature is below 25°C (77°F) then a heat source such as a light bulb placed near the sample can be used to increase the temperature. Use extreme caution with any method used to produce heat so a fire hazard is not created. Incubation above 35°C (95°F) must be prevented. Heat can destroy bacteria and could cause a false negative test outcome. Do not place the samples where they will receive direct sunlight as this may also cause a false negative outcome. Before leaving the testing site, remove any garbage from the collection process (i.e.-Media pouches and alcohol swabs, etc.) |
| 10 | Evaluate the reaction after 24 hours (Table 1). |  |
| 11 | Disposing of the Sample If you have cuts on your hands, ask someone else to perform this step. Dispose of the contents in the bottle in the same way human fecal matter is disposed of. Use the best sanitary practices available in your location. Sanitize your hands with hand sanitizer or wash hands vigorously with soap. |

Collecting and Preserving Samples

General Guidelines

Use proper sampling techniques to ensure seasonal variances are detected and the results are representative of the sample source. Avoid sample contamination during collection. Carefully open each sample container just prior to collection and close immediately following collection. Do not lay the cap down or touch the mouth or inside of the container. The PathoScreen medium contains sodium thiosulfate, so no dechlorination is necessary if the sample is added directly to the medium on site. Otherwise, treat samples to destroy chlorine residual and transport for analysis immediately after collection. Sodium thiosulfate sterilized within the collection container is commonly used to destroy chlorine residual. If samples cannot be analyzed immediately, label and store samples for up to 24 hours. In warm climates, maintain sample temperature between 4–10 °C (39–50 °F). Failure to properly collect and transport samples will cause inaccurate results.

Collecting from Faucets, Spigots, Hydrants, or Pumps

• Collect representative samples by allowing the water to run at a moderate rate (without splashing) for 2–3 minutes before sampling.

• Do not adjust rate of flow during sample collection.

• Avoid valves, spigots, or faucets that swivel or leak.

• Remove aerators or screens before sample collection.

Collecting from Rivers, Lakes, and Reservoirs

• Do not sample near the edge or bank.

• Remove the cap, hold the sample container near the bottom, and plunge the container mouth-down into the water. (This technique excludes surface scum.)

• While submerged, position the mouth of the container into the current.

• In non-flowing water, tilt the mouth of the container up slightly and allow it to fill slowly.

Some good communication practices to follow related to water quality testing

Do NOT:

- Say the water is “bad” or

- Say the water is “okay” until you have completed your testing

- Discuss test results with persons who are not in leadership in the community.

Do:

- Explain you are testing the water to make sure it is safe to drink

- Tell the local leaders you will evaluate the test results and discus the results with them at a later time

## Chapter 16:
Testing Water
for Turbidity

This chapter includes:

- Materials needed to build a turbidity tube

- Instructions for how to build a turbidity tube

- Instructions for how to test a water sample for turbidity

Purpose

If the turbidity in source water is too great, some water may not receive the minimum UV radiation dosage necessary to inactivate microbiological contaminants and the “treated” water may not be safe to drink.

Laboratory quality equipment to measure turbidity is expensive. The inexpensive and simple tool described in the following section provides a reasonably-accurate quantitative estimate of the level of turbidity well suited to our needs.

Materials needed

| Part No | Description | Qty |
| --- | --- | --- |
| 21 | Tube material – translucent, diameter 3 or 4 cm, 70 cm length | 1 |
| 22 | PVC end cap | 1 |
| Form 1 | Initial Assessment Form | 1 |

Tools needed

| Tool No | Description |
| --- | --- |
| 10 | Knife |
| 6 | Tape measure with metric markings |
| 18 | Black waterproof marker or black and white paint |

Testing Water Sample for Turbidity

| 1 | Mark viewing disc On the inside of the PVC end cap, draw the “Secchi disk” shown at the right using a waterproof marker or black and white paint. The lines of the Secchi disk must be sharp and straight. | Secchi disk |
| --- | --- | --- |
| 2 | Install end cap Cut the clear tube to a length of 70 cm. Put the PVC end cap on the tube. The cap should fit tightly so water cannot leak out. |
| 3 | Mark tube with NTU values Mark the tube with NTU values using these measurements. Begin measuring from the surface of the Secchi disk. See the diagram at the right. cm NTU 63.0 5 41.5 10 31.0 15 25.0 20 19.0 30 13.5 50 8.3 100 5.1 200 3.7 300 2.5 500 Measurements for the NTU markings on the turbidity tube were provided by Robens Centre for Public and Environmental Health at the University of Surrey in England. | Used by permission of Robert Rau, ©2004 |

Performing a Turbidity Test

- Stand with your back to the sun so the turbidity tube will be shaded.

- Pour water into the tube. Avoid creating bubbles, as these may cause false readings.

- Look straight down into the tube with your eye close to the tube opening.

- Stop adding water when the Secchi disk at the bottom of the tube is no longer visible. Rotate the tube slowly as you look to make sure you can not see the Secchi disk.

- Read the NTU marking nearest the water level.

- Record the NTU reading on Form 1, Initial Assessment, located in Appendix A

To meet the Vietnamese Ministry of Health DRINKING WATER HYGIENIC STANDARDS (Issued in accordance with the Decision No. 1329/2002/BYT/QD of Minister of health dated 18/4/2002), the turbidity must be equal to or less than 2 NTU.

If the turbidity is greater than 5 NTU for UV treatment to be effective, pretreatment of the source water is required.

## Chapter 17:
Testing Water
for Iron Content

This chapter includes:

- Materials needed to test a water sample for iron content

- Instructions for how to test a water sample for iron content

Purpose

A high concentration of iron in the water increases absorption of UV energy which may cause some water not to receive the minimum UV dosage to inactivate microbiological contaminants.

This test will determine the iron content of the water.

Tools needed

| Tool No | Description | Qty |
| --- | --- | --- |
| 19 | Iron Test Strip and Test Index Card | 1 |
| Form 1 | Initial Assessment Form | 1 |

Test Procedure

Follow the directions included with the Iron Test Kit.

Record the test result on Form 1, Initial Assessment Form

To meet the Vietnamese Ministry of Health DRINKING WATER HYGIENIC STANDARDS (Issued in accordance with the Decision No. 1329/2002/BYT/QD of Minister of health dated 18/4/2002), the iron content must be equal to or less than 0.5 mg/liter.

If the iron level is greater than 0.3 mg/l then pretreatment of the source water is required.

## Chapter 18:
Testing Water
for UV Transmissivity (UVT)

This chapter includes:

- Materials needed to build a UVT measurement reactor

- Instructions for how to build a UVT measurement reactor

- Instructions for how to test a water sample for UV Transmissivity

Purpose

Read Chapter 4 to understand the importance of UV Transmissivity (UVT) and how it is measured. In this chapter we will describe how to build the necessary equipment and make the UV measurements needed to calculate the UVT.

Materials needed

| Part No | Description | Qty |
| --- | --- | --- |
| 1 | Stainless Steel UV Reactor (see Chapter 8) | 1 |
| 22 | Quartz disc | 1 |
| 25 | Waterproof cement sealer | 1 |
| Form 1 | Initial Assessment Form | 1 |

Tools needed

| Tool No | Description |
| --- | --- |
| 2 | Digital Ultraviolet Radiometer |
| 1 | Electric drill – 3/8 inch or larger |
| 9 | 22 mm (7/8 inch) hole bit |
| 24 | Glove |

Building the UV Transmissivity Test Reactor

| 1 | Building the UVT test reactor Drill one 22mm (7/8 inch) hole in the middle of the bottom of the UV reactor Cement a quartz disc over the hole on the inside of the reactor. The seal must be watertight. Allow the cement to dry Rotate the elbows “up” to allow reactor to fill with water Fill the reactor with water and check for leaks. |  |
| --- | --- | --- |

UV Transmissivity Measurement Procedure

| 2 | Measuring UV energy Follow the instructions in Chapter 4 to make the two measurements needed to calculate the UVT. The chamber and the quartz window must be dry. Put the sensor of the radiometer against the quartz monitoring window in the bottom of the reactor. Rock the radiometer back and forth and record the highest reading. Note the glove on the hand holding the radiometer – the quartz window allows harmful UV energy to exit the reactor. |  |
| --- | --- | --- |

Record the results of the radiometer readings on Form 1, Initial Assessment Form

Perform the UVT calculations

After taking the two measurements described in this chapter return to Chapter 4 to complete the UVT calculations.

# Part 5:
Monitoring
and
Evaluation

## Chapter 19:
Reporting Water Quality
Test Results

This chapter includes:

- Materials and tools needed to report test results

- Instructions about procedures for reporting test results

Purpose

Testing water quality insures the UV treatment unit is operating correctly and providing safe water. The reporting procedure meets two important needs:

- reminds the system operator to test the water quality, and

- provides data to the water quality monitoring agency about the effectiveness of the regional UV water treatment program.

Materials needed

| Part No | Description | Qty |
| --- | --- | --- |
| Form 4 | Postcard response to report test results | 1 |
| 15 | Water quality test kit with instructions | 1 |

Reporting Water Quality Tests

| 1 | Reminder to test and return postcard Receive an envelop containing a reminder to test the water quality of your UV system and report the results to the monitoring office. |  |
| --- | --- | --- |
| 2 | Perform the test of water quality Use the test kit to perform the water quality test according to the instructions. See Chapter 10. |  |
| 3 | Report the test results Record the results of the test in the Water Quality Test Results Log. Fill in the information on the postcard you received in the mail. Then mail the postcard to the organization designated to monitor results in this region. |  |

## Chapter 20:
Reporting Problems

This chapter includes:

- Instructions for reporting problems

Purpose

Maintaining the UV water treatment system in proper working order is critical to achieving the outcomes the system is designed to produce.

The user of the system has the primary responsibility for reporting any problems with the system and then following through to insure that repairs are completed.

IMPORTANT: If you suspect a problem has caused the quality of the water to become unsafe to drink, stop using the system immediately. Notify the contact person to have the system inspected and repaired.

Materials needed

| Part No | Description | Qty |
| --- | --- | --- |
| Form 5 | System History Log | 1 |

Reporting Problems

| 1 | Update the System History Log. Fill in the required information in Form 5, System History Log in the Operation Problems and Solutions section. |
| --- | --- |
| 2 | Who to contact for help. Contact Name: Phone: Address: Email: |

# Appendix A:

Forms

## Form 1: Initial Assessment

| Site Name: Site Number: | Date: | Your Name: | picture |
| --- | --- | --- | --- |
| Province: District: Commune/Village: Health Clinic School (level) Household Other Avg daily population_____ Est. water usage/day_______ # water stations____ GPS Coordinates (WGS84): Latitude: N or S Longitude: E or W Names of contact persons/phone number/email: / / |

1. Current source for drinking water:

a.  Central distribution from piped system

b.  Dug well  1)  concrete lined  2)  unlined  3)  covered  4)  pad  5)   pump  6)  bucket

c.  Drilled well  1)  electric pump  2)  hand pump

d.  Driven well  1)  electric pump  2)  hand pump

e.  Surface water (river, stream or pond)       f.   Rain water

g.  Bottled water

h. Does water source ever become dry?  1)  yes   2)  no

i.  What is the distance of water source from the nearest latrine?        meters

j.  Is city (piped) water available nearby? 1)  yes   2)  no

2. Current treatment method: (check all that are used)

a.  Sand filter

b.  Boiling       Method:  1)  electricity 2)   wood or charcoal fire  3)  gas

c.  Ceramic filter

d.  Chlorine

e.  No treatment before use

f.   Other (describe)

3. Storage method for drinking water: (check all that are used)

a.  Cistern                  Type:  1)  covered  2)  uncovered

b.  Tank                      Type:  1)  plastic  2)  metal     3)  other

c.  Small Container    Type:  1)  plastic  2)  thermos  3)  other

4. Quality of raw source water

| color | odor | Turbidity (NTU) | Bacteria test (+ or -) | TDS (ppm-KCl) | Fe (ppm) | NO3 (ppm) | NO2 (ppm) | UV Irr (no water) | UV Irr (with water) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

5. Quality of pretreated water (if any – typically sand filtered)

| color | odor | Turbidity (NTU) | Bacteria test (+ or -) | TDS (ppm-KCl) | Fe (ppm) | NO3 (ppm) | NO2 (ppm) | UV Irr (no water) | UV Irr (with water) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

6. Organizations that have providing assistance with water and sanitation projects:

| None Self Help Local government agency | UNICEF Other Other |
| --- | --- |

7. Perceived Needs:

## Form 2: Follow-up Assessment

Use of UV Treatment System Assessment Form

| Site Name: | Date: | Site Number: | Your Name: |
| --- | --- | --- | --- |

GPS Coordinates (WGS84):   Latitude:  N         	Longitude:  E

Names of contact persons:

1. System Operation:

a. Is UV system currently in use? 1)   yes   2)   no  if “no”, why

b. Is practice of boiling continuing?  1)    yes  2)   no

c Are user instructions posted near the UV system?  1)   yes  2)   no

d Is the location of the UV system convenient for users? 1)   yes  2)   no

2. How many times each day is the UV system used to process water?

a.  none      b.  1      c.  2      d.  3     e.  more than 3     f. other

3. User Training on Operation:

Has primary user received adequate training?  a.  yes   b.  more training needed

Is a backup user trained to operate the UV treatment system?  a.  yes   b.  no

4. User Training on Water Quality Testing:

Has primary user adequately trained?  a.   yes     b.   more training needed

5. Frequency of Testing Water Quality

How often is the water tested?  a.  never   b.  weekly  c.  monthly  d. other

6. Write here any comments from the user.

7. Do you observe any physical problems? (e.g., leaks, cracks, etc.)

8. Do you observe any operating problems?

9. Test Results of Flow Rate and Water Quality:

Measured Flow Rate: a.          Maximum Allowable Flow Rate: b.

Result of test for microbiological contamination in treated water

c.   present    d.   absent   e. Date:

10. Comments:

## Form 3: Water Quality Test Results Log

Results of H2S test for presence or absence of bacteria in treated water

| Site Name: | Date Installed: | Site Number: |
| --- | --- | --- |

GPS Coordinates (WGS84):   Latitude:  N         	Longitude:  W or E

| Date and Time of Test | Result after 24 hours (circle one) | Result after 48 hours (circle one) | Name of Tester |
| --- | --- | --- | --- |
|  | OK (yellow) Not OK (black) | OK (yellow) Not OK (black) |  |
|  | OK (yellow) Not OK (black) | OK (yellow) Not OK (black) |  |
|  | OK (yellow) Not OK (black) | OK (yellow) Not OK (black) |  |
|  | OK (yellow) Not OK (black) | OK (yellow) Not OK (black) |  |
|  | OK (yellow) Not OK (black) | OK (yellow) Not OK (black) |  |
|  | OK (yellow) Not OK (black) | OK (yellow) Not OK (black) |  |
|  | OK (yellow) Not OK (black) | OK (yellow) Not OK (black) |  |
|  | OK (yellow) Not OK (black) | OK (yellow) Not OK (black) |  |
|  | OK (yellow) Not OK (black) | OK (yellow) Not OK (black) |  |
|  | OK (yellow) Not OK (black) | OK (yellow) Not OK (black) |  |
|  | OK (yellow) Not OK (black) | OK (yellow) Not OK (black) |  |
|  | OK (yellow) Not OK (black) | OK (yellow) Not OK (black) |  |
|  | OK (yellow) Not OK (black) | OK (yellow) Not OK (black) |  |
|  | OK (yellow) Not OK (black) | OK (yellow) Not OK (black) |  |
|  | OK (yellow) Not OK (black) | OK (yellow) Not OK (black) |  |
|  | OK (yellow) Not OK (black) | OK (yellow) Not OK (black) |  |
|  | OK (yellow) Not OK (black) | OK (yellow) Not OK (black) |  |

## Form 4: Water Quality Test Reporting

On the first Monday of the month, perform the test of water quality according to the instructions. After the test is completed, fill in the following information on this postcard  and then mail the postcard. Please print all information.

| Site Name: | Site Number: | Other Location Information: |
| --- | --- | --- |
| Date of Test: | Printed Name of Person Performing Test: Signature of Person Performing Test: |
| Result of Test: Absence of bacteria Presence of bacteria | How many tests can you perform in the future with the supplies currently on hand? Comments: |

To: UV Water Treatment Test Monitor Name of Monitoring Agency Post Office Box 1234 City, Province Country

## Form 5: UV Treatment System History Log

| Site Name: | Site Number: | Other Location Information: |
| --- | --- | --- |

- Installation

| Name of installer | Date of installation | Describe model and features installed | Maximum allowable flow rate |
| --- | --- | --- | --- |

- Training

| Name of trainer | Date of training | Names of persons trained | Comments |
| --- | --- | --- | --- |
| Name of trainer | Date of training | Names of persons trained | Comments |

Document additional training on extra sheets

- Operation Problems and Solutions

| Name of person identifying problem | Date of problem | Describe the problem | How was the problem resolved? |
| --- | --- | --- | --- |
| Name of person identifying problem | Date of problem | Describe the problem | How was the problem resolved? |

Document additional problems on extra sheets

- Maintenance and UV Lamp Replacement

| Name of person performing maintenance | Date of maintenance | Describe work completed. If UV lamp replaced, record new output at 40 mm in µW-sec/cm2 | Why was this work performed? |
| --- | --- | --- | --- |

Document additional maintenance on extra sheets

## Form 6: Parts and Tools Inventory Form

| Part Number # | Part Name | Description |
| --- | --- | --- |
| Model Number | Important Criteria / number needed |
| Cost | Where to buy / Business Name / Address / GPS coordinates |
| Photo | Comments |

| Part Number # | Part Name | Description |
| --- | --- | --- |
| Model Number | Important Criteria / number needed |
| Cost | Where to buy / Business Name / Address / GPS coordinates |
| Photo | Comments |

# Appendix B:

Parts Inventory

| Part Number 1 | Part Name Ultraviolet Treatment Unit | Description Ultraviolet reactor and cover with UV lamp mountings and power supply |
| --- | --- | --- |
| Model Number Custom built | Important Criteria / number needed Stainless steel construction Built to exact specifications of plans Quantity – 1 |
| Cost Vietnam – 2005 -- 165,000 dong 2006 – 190,000 dong | Where to buy / Business Name / Address / GPS coordinates Phuoc Phoung 115 (#14) Ong Ich Khiem, Hue N 16( 28.293 E 107( 35.102 |
|  | Comments |

| Part Number 2 | Part Name UV Germicidal Lamp | Description Ultraviolet germicidal lamp |
| --- | --- | --- |
| Model Number Sankyo Denki Co, Ltd G8T5 | Important Criteria / number needed Length 30 cm 8 watts Must be “germicidal” UV Quantity – 1 |
| Cost Vietnam – not currently available In US -- $5.10 plus shipping and tax | Where to buy / Business Name / Address / GPS coordinates TEC/WEST (U.S.A.), Inc. 6344 Arizona Circle Los Angeles, CA 90045 +1 (800) 421-7215 x 200 info@tecwest.com http://www.tecwest.com/lighting/germicidal.html |
|  | Comments Tec/West has successfully FedExed to our office in Vietnam Distributorships can be established by contacting the lamp manufacturer directly at Sankyo Denki Co., Ltd Export Dep't., No. 1908, Shin-Aoyama Bldg., 1-1-1 Minami, Aoyama, Minato-ku, Tokyo, Japan Phone 81-03-3402-4141 |

| Part Number 3 | Part Name Lamp connectors | Description Electrical connectors for UV lamp (sometimes called “lamp hangers” or “end caps”) |
| --- | --- | --- |
| Model Number none | Important Criteria / number needed Fits G8T5 UV lamp Quantity -- 2 |
| Cost 2,000 dong each | Where to buy / Business Name / Address / GPS coordinates Ask for Mr. Phú Quang Phu Electric store 136 Lê Quang Định, P.14, Q. Bình Thạnh, TP. HCM Phone: 08-414-473 Mobile: 0913-930-1963 |
|  | Comments |

| Part Number 4 | Part Name Transformer | Description Electrical transformer |
| --- | --- | --- |
| Model Number 503 Manufacturer: QP 323 Hoang Van Thu, Hanoi (new location – ask Mrs Ha) | Important Criteria / number needed 220 volts, 40 watt 4 wires for lamps Quantity – 1 Dimensions – 4 cm by 3 cm by 15 cm |
| Cost 19,000 to 20,000 dong | Where to buy / Business Name / Address / GPS coordinates Tung Hong 35 Nguyen Sinh Cung, Vy Da, Hue N 16( 28.541 E 107( 35.724 Morning Star Company 27 Hoang Sam, Hanoi. |
|  | Comments Very common in Vietnam Used for fluorescent lamps Made in Vietnam 20watt model will work but not as good |

| Part Number 5 | Part Name Power Cord | Description Power cord for transformer |
| --- | --- | --- |
| Model Number none | Important Criteria / number needed Vietnam style 220 Volt plug Two wire Length – 3 meters |
| Cost 6,500 dong | Where to buy / Business Name / Address / GPS coordinates Tung Hong 35 Nguyen Sinh Cung, Vy Da, Hue N 16( 28.541 E 107( 35.724 |
|  | Comments |

| Part Number 6 | Part Name Container | Description Sand filter container Safe water storage container |
| --- | --- | --- |
| Model Number none | Important Criteria / number needed Plastic, 20 liters, large open top at least 11 cm Flat sides to minimize leakage Height 45 cm, width 25 cm, depth 25 cm Quantity -- 2 |
| Cost 30,000 dong each $1.95 US | Where to buy / Business Name / Address / GPS coordinates Vendor – Lam Dong Ba Cho N 16( 28.312 E 107( 35.304 |
|  | Comments Substitute -- water container – must sanitize with chlorine wash NOT boiling water Buy at 29 Tran Thuc Nhan – Thanh Pho, Hue 054 826307 – cost about 30,000 dong |

| Part Number 7 | Part Name Elbow fittings | Description Water tight plastic fitting to connect to tubing |
| --- | --- | --- |
| Model Number none | Important Criteria / number needed Rubber ‘O’ rings for water tight seal Locking nut Quantity – 4 21mm inside diameter for PVC connection |
| Cost 4,200 dong each (2006) | Where to buy / Business Name / Address / GPS coordinates Phuc Hung 137 Huynh Thuc Khang, Hue, Vietnam N 16( 28.632 E 107( 35.181 |
|  | Comments The rubber washers and nut assembly looks like this when purchased. |

| Part Number 8 | Part Name Valve | Description Flow control valve for UV treatment inlet |
| --- | --- | --- |
| Model Number none | Important Criteria / number needed Diameter – fits tubing Quantity -- 1 |
| Cost 6,000 dong (2006) | Where to buy / Business Name / Address / GPS coordinates Phuc Hung 137 Huynh Thuc Khang, Hue, Vietnam N 16( 28.632 E 107( 35.181 |
|  | Comments |

| Part Number 9 | Part Name Flow Restrictor | Description Flow control restriction device |
| --- | --- | --- |
| Model Number Custom built | Important Criteria / number needed Diameter – fits inside valve body Hole diameter = 3.5 mm (9/64 inch) Quantity -- 1 |
| Cost minimal | Where to buy / Business Name / Address / GPS coordinates |
|  | Comments A US penny is the correct size Vietnamese 1,000 dong coin is also correct size.. |

| Part Number 10 | Part Name Tubing | Description |
| --- | --- | --- |
| Model Number none | Important Criteria / number needed Flexible and Clear Length – 1 meter Diameter, inside – 20 mm |
| Cost 6,000 dong per meter | Where to buy / Business Name / Address / GPS coordinates Dung Huong 93 Huynh Thuc Khang St, Hue N 16( 28.569 E 107( 35.211 |
|  | Comments |

| Part Number 11 | Part Name Sand | Description Sand, type quartz |
| --- | --- | --- |
| Model Number none | Important Criteria / number needed As clean as possible Small grains Quantity – 0.25 m3 |
| Cost 5,000 dong | Where to buy / Business Name / Address / GPS coordinates |
| Photo | Comments |

| Part Number 12 | Part Name Filter Pipe | Description Slotted filter pipe inside inflow container |
| --- | --- | --- |
| Model Number none | Important Criteria / number needed Length - 25 cm Minimum diameter – 5 cm |
| Cost 7,500 dong 60,000 dong / 2 meters | Where to buy / Business Name / Address / GPS coordinates Dung Huong 93 Huynh Thuc Khang St, Hue N 16( 28.569 E 107( 35.211 |
|  | Comments Exact diameter is not important |

| Part Number 13 | Part Name Filter Pipe ‘O’ Ring | Description ‘O’ ring that prevents sand from leaving the sand filter |
| --- | --- | --- |
| Model Number none | Important Criteria / number needed Quantity = 1 Flexible, easy to install Same diameter as Filter Pipe |
| Cost minimal | Where to buy / Business Name / Address / GPS coordinates various |
|  | Comments Many possible solutions; be creative. The foam padding used on motorcycle seats works well |

| Part Number 14 | Part Name Filter Pipe End Cap | Description End cap that prevents sand from leaving the sand filter container |
| --- | --- | --- |
| Model Number none | Important Criteria / number needed |
| Cost 1,000 dong | Where to buy / Business Name / Address / GPS coordinates Shop across the street from pCERWASS in Hue. |
|  | Comments Many possible solutions; be creative. It is possible to use Part 13, Filter Pipe “O” Ring in place of this part – installation is more difficult but end result works fine when both “O” rings are properly positioned so that sand does not leak out |

| Part Number 15 | Part Name Water Quality Test Supplies | Description Water Quality test supplies |
| --- | --- | --- |
| Model Number Hach Company Pathoscreen Field Test Kit 28591-00 Medium pillows only 26107-96 | Important Criteria / number needed Each kit contains media for 100 tests |
| Cost From Hach in US - $ 0.30 USD per test From Hach distributor in Vietnam -- $ 0.?? per test | Where to buy / Business Name / Address / GPS coordinates Special order from HCMC – Hach Distributor Cong ty Co Phan Thiet Bi Thi Viet 2-4 Thach Thi Thanh , Quan 1 TP HCMC Phone 08 8209326 Fax 08 8209319 Mobile 0903 940887 email dinhhien@thiviet.com Or order from US website www.hach.com |
|  | Comments |

| Part Number 16 | Part Name Label | Description Label for side of inflow container |
| --- | --- | --- |
| Model Number none | Important Criteria / number needed “UV Safe Water” and same in Vietnamese |
| Cost 15,000 dong | Where to buy / Business Name / Address / GPS coordinates Thanh Cong Design 21-37 Ngo Quyen Hue (054) 847978 |
|  | Comments Add operations instructions / reduce logo size as needed |

| Part Number 15 | Part Name Water Quality Test Supplies | Description Water Quality test supplies |
| --- | --- | --- |
| Model Number Hach Company Pathoscreen Field Test Kit 28591-00 Medium pillows only 26107-96 | Important Criteria / number needed Each kit contains media for 100 tests |
| Cost From Hach in US - $ 0.30 USD per test From Hach distributor in Vietnam -- $ 0.?? per test | Where to buy / Business Name / Address / GPS coordinates Special order from HCMC – Hach Distributor Cong ty Co Phan Thiet Bi Thi Viet 2-4 Thach Thi Thanh , Quan 1 TP HCMC Phone 08 8209326 Fax 08 8209319 Mobile 0903 940887 email dinhhien@thiviet.com Or order from US website www.hach.com |
|  | Comments |

| Part Number 16 | Part Name Label | Description Label for side of inflow container |
| --- | --- | --- |
| Model Number none | Important Criteria / number needed “UV Safe Water” and same in Vietnamese |
| Cost 15,000 dong | Where to buy / Business Name / Address / GPS coordinates Thanh Cong Design 21-37 Ngo Quyen Hue (054) 847978 |
|  | Comments Add operations instructions / reduce logo size as needed |

| Part Number 17 | Part Name System Stand | Description System stand made of PVC pipe and fittings |
| --- | --- | --- |
| Model Number Custom built | Important Criteria / number needed 21 mm OD PVC pipe – 7 meters T’s to fit PVC pipe – qty – 20 Elbows to fit PVC pipe – qty – 16 Container of PVC cement |
| Cost 122,000 dong | Where to buy / Business Name / Address / GPS coordinates Phuc Hung 137 Huynh Thuc Khang (54) 512-137 |
|  | Comments In USA, this type PVC pipe is referred to as “Sch 40” |

| Part Number 18 | Part Name Diffuser Plate | Description Plate in top of sand filter to minimize disturbing sand when water is added to the container. |
| --- | --- | --- |
| Model Number custom made | Important Criteria / number needed About 25 cm in diameter Flexible plastic -- can not float in water About 30 or 40 holes of diameter 2-3 mm |
| Cost minimal | Where to buy / Business Name / Address / GPS coordinates |
|  | Comments This piece can be made from a variety of materials – be creative |

| Part Number 19 | Part Name UV Warning Label | Description Warning label describing eye and skin dangers from exposure to ultraviolet radiation. |
| --- | --- | --- |
| Model Number custom made | Important Criteria / number needed Text in local language |
| Cost | Where to buy / Business Name / Address / GPS coordinates |
|  | Comments Black letters on yellow background |

| Part Number 20 | Part Name Sheet Metal Screws | Description Sheet metal screws |
| --- | --- | --- |
| Model Number none | Important Criteria / number needed # 10 or 12, length 25-30 mm – qty - 3 # 10 or 12, length 10 mm – qty - 2 |
| Cost minimal | Where to buy / Business Name / Address / GPS coordinates various |
|  | Comments Longer screws for leveling UV unit Shorter screws for UV unit shield |

| Part Number 21 | Part Name Tubing | Description Clear plastic tube, diameter 3 to 4 cm, length 70 cm |
| --- | --- | --- |
| Model Number none | Important Criteria / number needed Qty – 1 per system builder Used for Turbidity Tube |
| Cost $ 1.50 US | Where to buy / Business Name / Address / GPS coordinates Clear Polycarbonate Tube Lamp Guard, Lithonia Lighting, Conyers, GA 30012 http://www.lithonia.com/sitetools/contact.asp |
| Comments Glass tubing could be a safety hazard Substitute material OK Divide into three sections for easy transport; use PVC joints to reconnect |

| Part Number 22 | Part Name PVC End Cap | Description End cap for Part 21, diameter must be correct to make a water tight seal |
| --- | --- | --- |
| Model Number none | Important Criteria / number needed Qty – 1 per system builder |
| Cost $1 US | Where to buy / Business Name / Address / GPS coordinates Any hardware store in US |
|  | Comments See Chap 16 for use |

| Part Number 23 | Part Name Spigot | Description Safe water storage container spigot |
| --- | --- | --- |
| Model Number none | Important Criteria / number needed Quantity – 1 |
| Cost 20,000 dong (2006) | Where to buy / Business Name / Address / GPS coordinates Dung Huong 93 Huynh Thuc Khang St, Hue N 16( 28.569 E 107( 35.211 |
| Comments |

| Part Number 24 | Part Name Bleach | Description Bleach, liquid |
| --- | --- | --- |
| Model Number none | Important Criteria / number needed 0.5 liters Should be “fresh”; not old |
| Cost 10,000 dong | Where to buy / Business Name / Address / GPS coordinates Local market |
|  | Comments |

| Part Number 25 | Part Name Silicone Sealant | Description Silicone Sealant, waterproof |
| --- | --- | --- |
| Model Number none | Important Criteria / number needed |
| Cost 20,000 dong | Where to buy / Business Name / Address / GPS coordinates |
|  | Comments |

| Part Number 26 | Part Name Hand Sanitizer and Alcohol Sanitizing Swab | Description Container of Hand Sanitizer Alcohol Sanitizing Swabs |
| --- | --- | --- |
| Model Number varies | Important Criteria / number needed Contains 65-70% alcohol |
| Cost varies | Where to buy / Business Name / Address / GPS coordinates Local market |
|  | Comments |

| Part Number 27 | Part Name Electrical Tape and Wire Nuts | Description Electrical tape and wire nuts |
| --- | --- | --- |
| Model Number none | Important Criteria / number needed Wire nuts must be correct size for electrical wire used |
| Cost | Where to buy / Business Name / Address / GPS coordinates Local market |
|  | Comments |

| Part Number 28 | Part Name Rubber Grommet | Description Rubber grommet |
| --- | --- | --- |
| Model Number none | Important Criteria / number needed Size must fit size of wire used Qty - 2 |
| Cost | Where to buy / Business Name / Address / GPS coordinates Local market |
| Photo | Comments |

# Appendix C:

Tool Inventory

| Tool Number 1 | Tool Name Electric Drill | Description Electric drill |
| --- | --- | --- |
| Model Number | Important Criteria / number needed 220 volts |
| Cost | Where to buy / Business Name / Address / GPS coordinates Local market |
|  | Comments |

| Tool Number 2 | Tool Name Digital Ultraviolet Radiometer | Description Radiometer measuring UV energy in the 254 nanometer range |
| --- | --- | --- |
| Model Number Solarmeter 8.0 | Important Criteria / number needed One |
| Cost $199 US | Where to buy / Business Name / Address / GPS coordinates Solartech Inc. 26101 Harbour Pointe Dr N. Harrison Twp, MI 48045 USA US (800) 798-3311 http://www.solarmeter.com/index.html |
|  | Comments This model’s UV irradiance measurement maximum is 2,000 µW/cm2 |

| Tool Number 3 | Tool Name Lighter | Description Lighter |
| --- | --- | --- |
| Model Number | Important Criteria / number needed |
| Cost | Where to buy / Business Name / Address / GPS coordinates Local Market |
|  | Comments Used to heat tubing |

| Tool Number 4 | Tool Name Level | Description Small level |
| --- | --- | --- |
| Model Number | Important Criteria / number needed 15-20 cm in length |
| Cost | Where to buy / Business Name / Address / GPS coordinates Local Market |
|  | Comments |

| Tool Number 5 | Tool Name PVC Cutter | Description PVC Cutter |
| --- | --- | --- |
| Model Number | Important Criteria / number needed |
| Cost | Where to buy / Business Name / Address / GPS coordinates Local market |
|  | Comments If not available, various types of saws can be used |

| Tool Number 6 | Tool Name Tape Measure | Description Tape measure |
| --- | --- | --- |
| Model Number | Important Criteria / number needed Markings in centimeters |
| Cost | Where to buy / Business Name / Address / GPS coordinates Local market |
|  | Comments Optional – markings in inches |

| Tool Number 7 | Tool Name Screw Driver | Description Screw driver |
| --- | --- | --- |
| Model Number | Important Criteria / number needed Text |
| Cost | Where to buy / Business Name / Address / GPS coordinates Local market |
|  | Comments Regular or Phillips head depending on type of screws used |

| Tool Number 8 | Tool Name Hack Saw | Description Hack saw |
| --- | --- | --- |
| Model Number | Important Criteria / number needed |
| Cost | Where to buy / Business Name / Address / GPS coordinates Local market |
|  | Comments Used to cut filter pipe |

| Tool Number 9 | Tool Name Drill Bits | Description Drill bits |
| --- | --- | --- |
| Model Number | Important Criteria / number needed 22 mm (7/8 inch) Bi-metal hole drill for drilling sheet metal 3 mm (1/8 inch) 3.5 mm (9/64 inch) drill bit for flow restrictor hole Spade bit, 19 mm (3/4 inch) Spade bit, 15 mm (5/8 inch) |
| Cost | Where to buy / Business Name / Address / GPS coordinates Local market |
|  | Comments |

| Tool Number 10 | Tool Name Knife | Description Knife |
| --- | --- | --- |
| Model Number | Important Criteria / number needed |
| Cost | Where to buy / Business Name / Address / GPS coordinates Local market |
|  | Comments Used to cut tubing |

| Tool Number 11 | Tool Name 18 Sieve Screen | Description Number 18 sieve screen |
| --- | --- | --- |
| Model Number | Important Criteria / number needed Mesh count – 8 threads per cm / 18 threads per inch |
| Cost | Where to buy / Business Name / Address / GPS coordinates Local market |
| picture | Comments Used to sift sand for filter Window screen is approximately the correct size Sand particles too large to pass through this sieve should be discarded |

| Tool Number 12 | Tool Name 45 Sieve Screen | Description Number 45 sieve screen |
| --- | --- | --- |
| Model Number | Important Criteria / number needed Mesh count – 20 threads per cm / 45 threads per inch |
| Cost | Where to buy / Business Name / Address / GPS coordinates |
| picture | Comments Used to sift sand for filter Mosquito netting is approximately the correct size Sand particles small enough to pass through this sieve should be discarded |

MEDRIX Ultraviolet Water Treatment System

| Tool Number 13 | Tool Name ?? Sieve Screen | Description Number ?? sieve screen for sizing pea gravel |
| --- | --- | --- |
| Model Number | Important Criteria / number needed Text |
| Cost | Where to buy / Business Name / Address / GPS coordinates |
| picture | Comments This item may be deleted |

| Tool Number 14 | Tool Name Respirator Mask | Description Respirator mask to prevent inhaling dust during screening of sand |
| --- | --- | --- |
| Model Number | Important Criteria / number needed |
| Cost | Where to buy / Business Name / Address / GPS coordinates Local market |
|  | Comments Used when sifting sand for filter |

| Tool Number 15 | Tool Name Pop riveter | Description Pop riveter |
| --- | --- | --- |
| Model Number | Important Criteria / number needed |
| Cost | Where to buy / Business Name / Address / GPS coordinates Local Market |
|  | Comments |

| Tool Number 16 | Tool Name Soldering iron | Description Soldering iron |
| --- | --- | --- |
| Model Number | Important Criteria / number needed 220 volts |
| Cost | Where to buy / Business Name / Address / GPS coordinates Local market |
|  | Comments Also need solder |

| Tool Number 17 | Tool Name Turbidity tube | Description Turbidity tube |
| --- | --- | --- |
| Model Number | Important Criteria / number needed |
| Cost | Where to buy / Business Name / Address / GPS coordinates This item is constructed by the user. See Chapter 16 for instructions |
|  | Comments |

| Tool Number 18 | Tool Name Black Marker Pen | Description Black marker pen, waterproof |
| --- | --- | --- |
| Model Number | Important Criteria / number needed |
| Cost | Where to buy / Business Name / Address / GPS coordinates Local market |
|  | Comments |

| Tool Number 19 | Tool Name Iron Test | Description Iron Test Strip and Test Index Card |
| --- | --- | --- |
| Model Number 480125 ITS | Important Criteria / number needed |
| Cost | Where to buy / Business Name / Address / GPS coordinates Industrial Test Systems (01) 800-861-9712 www.sensafe.com |
|  | Comments |

| Tool Number 20 | Tool Name Watch | Description Watch with second hand |
| --- | --- | --- |
| Model Number | Important Criteria / number needed |
| Cost | Where to buy / Business Name / Address / GPS coordinates Local market |
|  | Comments This part is used to measure water output flow rates |

| Tool Number 21 | Tool Name Measuring Container | Description One liter measuring container |
| --- | --- | --- |
| Model Number | Important Criteria / number needed Markings in liters |
| Cost | Where to buy / Business Name / Address / GPS coordinates Local market |
|  | Comments This part is used to measure water output flow rates |

| Tool Number 22 | Tool Name Quartz Disc | Description Quartz disc, ground and polished for measuring UV irradiance |
| --- | --- | --- |
| Model Number Item # 1X0.062 | Important Criteria / number needed 1 inch diameter by 1/16 inch thickness |
| Cost $4.70 US plus shipping | Where to buy / Business Name / Address / GPS coordinates TECHNICAL GLASS PRODUCTS, INC. Sales and Engineering Facility 881 Callendar Blvd. Painesville Twp., OH 44077 PHONE 440.639.6399 FAX 440.639.1292 email: tgp@tgpohio.com http://www.technicalglass.com/ |
|  | Comments This part is used to construct one UV reactor for use in testing described in Chapters 4 and 18 |

| Tool Number 23 | Tool Name Boiling Water Device | Description Kettle for boiling water, electric, light weight |
| --- | --- | --- |
| Model Number | Important Criteria / number needed Text |
| Cost | Where to buy / Business Name / Address / GPS coordinates Local Market |
|  | Comments Text |

| Tool Number 24 | Tool Name Glove | Description Glove |
| --- | --- | --- |
| Model Number none | Important Criteria / number needed Must not transmit UV energy (use radiometer to check) |
| Cost Varies | Where to buy / Business Name / Address / GPS coordinates Local market |
|  | Comments |

# Appendix D:
The Science of Ultraviolet Energy and Water Treatment

This appendix contains some technical descriptions of how ultraviolet energy works for the purpose of water treatment.

Definitions

Understanding the effects of UV-C energy on microorganisms requires a certain vocabulary, and the words used have specific definitions. The following are key concepts integral to understanding UV radiation and water treatment.

Residence Time  Residence time is the specific length of time during which an microorganism is exposed to UV-C radiation while passing through the UV chamber. Residence time varies depending on the specific path the organism follows through the chamber.

Dosage  The dosage is a function of the amount of UV-C energy emitted (expressed in power or microwatts) over a specific area (expressed in square centimeters) delivered for a given residence time (expressed in seconds).  The effectiveness of a UV disinfection system depends on the dosage of UV radiation delivered to the water.

Formula 1:  UV Dosage (microwatt-sec/cm2) = (Power (µW) / Area (cm2)) x Time (sec)

Appendix G summarizes the different dosages of UV energy needed to inactivate various microorganisms. Because it is difficult to identify every microorganism present in a water source, it is also difficult to specify a minimum UV dosage requirement that will satisfy all situations. As mentioned in Chapter 4, 30,000 µW-sec/cm2 is the widely accepted international guideline for UV disinfection of water.  MEDRIX has adopted this guideline as the minimum dosage requirement for operation of a MEDRIX UV Water System unless the country where this system is used has a higher guideline.

Irradiance  The “power per unit area” term from Formula 1 is also called “irradiance.” UV irradiance at a specific point is a function of:

- the UV power and efficiency of the lamp

- the UV absorbing and reflecting properties of the air and water between a given point and the lamp.

- any UV energy reflected from surfaces of the chamber

UV irradiance can be determined using a radiometer designed to measure UV energy in the 254 nm (UV-C) range. Tool #2 in Appendix C is an example of this type of radiometer.

Transmittance and Absorbance Dissolved substances in the water—especially iron, organic carbon and nitrates—can absorb UV energy as explained in Chapters 2 and 3. Transmittance is a measure of how much UV energy passes through a water sample, while absorbance quantifies the amount of UV energy unable to pass through. Absorption and transmissivity are inversely related; the higher UV absorption, the lower the transmissivity. This is important because high absorbance (low transmissivity) reduces the potential for UV irradiance to inactivate microorganisms at all depths in the water.

Turbidity also plays a role in the transmittance of UV energy. Particles in water causing turbidity can block or reflect UV radiation, effectively shielding microorganisms and preventing the microorganisms from receiving full exposure to the UV irradiation. However, until turbidity exceeds 5 NTUs, as explained in Chapters 2 and 3, this effect is usually insignificant.

Measuring Dosage in a UV Reactor

A radiometer measures UV irradiance at a specific point. Since, it can only measure irradiance coming from a narrow acceptance angle (i.e. from a specific direction) and not from 360 degrees, it is difficult to estimate the total UV dosage provided in a particular disinfection chamber. With this limitation in mind, we will approximate the UV dosage for a given system configuration based on several key assumptions.

ASSUMPTION 1 – The UV radiation chamber can be characterized using a mean dosage computed from the UV irradiance at approximately mid-level in the water. This assumption accounts for UV energy absorption in the water sample.

Formula 2:	Irradiancemid-level = (Irradiancetop of water + Irradiancebottom of water) / 2

Detail instructions for computing this mid-level irradiance value are located in Addendum 1 at the end of this appendix.

ASSUMPTION 2 – A “Disinfect Zone” can be identified in the treatment chamber where most of the effective UV treatment occurs. The volume of the irradiation “Disinfect Zone” (VDZ) is the cross-sectional area of the reactor chamber times the distance measured at the bottom of the reactor parallel to the lamp where UV irradiance exceeds 80% of maximum irradiance of the lamp.

In the reactor design used in this handbook, the VDZ is 0.8 liters according to lab-measured UV irradiance values.

ASSUMPTION 3 – The water flowing through the reactor is uniformly mixed during passage through the reactor. This implies that all microorganisms in the water will have the same residence time in the reactor and will receive the same overall UV dosage.

Calculating UV Dosage

Approximate the UV dosage by multiplying the “mid-level” irradiance by the residence time of a microorganism in the “disinfect zone” of the radiation chamber. Residence time is a function of the water flow rate and the “disinfect zone” volume.

Formula 3 is used to compute a UV dosage value given a specified water flow rate.

Formula 3:

UV Dosage = Irradiancemid-level x VDZ (liters) x 60 sec/min / Flow Rate (l/min)

Example Use Formulas 2 and 3 to calculate the UV dosage delivered at a flow rate of 2 liters per minute. Assume irradiance at the bottom of the reactor chamber filled with source water is measured at 900 µW / cm2. Assume irradiance at the top of the water is 2,000 µW / cm2 (see Addendum 1).

Irradiance mid-level		= 1450 µW / cm2

VDZ				= 0.8 liters

Flow Rate			= 2.0 liters per minute

UV Dosage = 1450 X 0.8 X 60 / 2 = 34,800 µW-sec/cm2

Calculating Maximum Flow Rate

Conversely, select a UV dosage value you wish to achieve and compute the maximum flow rate allowable for water passing through the reactor chamber.

Formula 4:	Flow Rate = (Irradiancemid-level x VDZ x 60 sec/min) / Dosage

Example  Use Formulas 2 and 4 to calculate the flow rate required to obtain a UV dosage of 30,000 µW-sec/cm2.

Irradiancemid-level = 1450 µW/cm2

Max flow rate = 1450 µW/cm2 x 0.8 liters x 60 / 30,000 µW-sec/cm2 = 2.3 l/min

This result implies that effective UV water treatment, meeting the internationally recognized dosage guideline, is possible if the flow rate is restricted to no more than 2.3 liters per minute.

ADDENDUM 1: Estimating UV Irradiance Mid-Level in the Reactor Chamber

Measuring Irradiancebottom of water

To measure UV irradiance through the water at the bottom of the reactor chamber, you must construct a test chamber following the instructions in Chapter 18, Testing Water Samples for UV Transmissivity.

Using the test chamber and a radiometer, measure UV irradiance through the water at the bottom of the reactor chamber. A typical irradiance measurement through the quartz window for good quality water is about 900 µW/cm2.

Figure 3: Reactor chamber modified to measure UV transmissivity

Measuring Irradiancetop of water

Reading the UV irradiance at the top of the water is  an awkward measurement to make because it requires reading the radiometer deep inside the UV system. We will make this difficult reading once and then, for the future, devise a simpler method to reliably compute the UV irradiance at the top of the water.

Make a one-time measurement of UV irradiance at the position where the top of the water would be. This operation must be performed with great care and only needs to done once. With the UV lamp “off”, calculate the distance between the lamp and the top of the outlet baffle in the lower chamber. You will need to be creative, make several measurements and perform some additions and subtractions to determine the correct distance the water is from the UV lamp when the system is operating.

Next, remove the chamber cover, plug in the UV lamp and allow the lamp to warm up for 2 minutes. While protecting your skin and eyes from UV exposure, positioning the radiometer inside the chamber cover at the distance from the lamp that you calculated where the top of the water would be. Read the UV irradiance value measured by the radiometer.

The actual UV irradiance measured at the surface of the water in the “disinfect zone” for the UV G8T5 lamp used in our test system exceeded 2,000 µW/cm2.

Replace the chamber cover and take another reading of UV irradiance through the quartz window in the bottom of the chamber with no water present. For example, our measurements were:

Irradiancetop of water		2,000 µW/cm2

Irradiancebottom with no water 	1,160 µW/cm2

Difference		   840 µW/cm2

In the future, the UV Irradiancetop of water can now be accurately estimated by measuring the irradiance through the quartz window at the bottom of the reactor with no water present and then adding 840 µW/cm2 to that measured value.

Make these measurements in your UV system to determine the “difference value” for your configuration.

# Appendix E:
Glossary of Terms

Absorption - the transformation of UV light to other forms of energy as it passes through a substance.

Flow Rate - The volume of fluid flowing past a given cross sectional area per second. A common measurement unit is liters per minute.

Irradiance – The rate at which UV energy strikes a unit area (e.g., 1 cm2) in the water and described in terms of UV power per unit area, e.g., microwatts per square centimeter (μW / cm2)

Log Reduction - A 3-log reduction means a reduction in the number of microorganisms by 99.9%. For example, if water contained 1000 microorganisms, a 3-log reduction would reduce the number of microorganisms to 1.

Media Pillow - The plastic container holding the nutrient material that promotes growth of bacteria

Reactor - The chamber containing water being irradiated with UV energy.

NTU – Nephelometric Turbidity Unit  - a commonly-used unit of measurement for turbidity

Source Water – water taken directly from its source (e.g., stream, well, tank, etc.) before any treatment has been applied

Turbidity - cloudiness or haziness of water caused by individual particles too small to be seen without magnification

UV Dosage -: The energy is quantified to a dose by multiplying the UV Irradiance by the actual exposure time: Dose (μW sec/ cm2) = UV Irradiance (μW/ cm2) x Time (seconds)

UV Transmittance (UVT) - The ability of water to allow UV light to pass through. Transmittance of a water sample is measured as the percentage (%T) of transmitted light (I) to light striking the surface (I0) through a defined path length (L). Many naturally occurring organic and inorganic constituents (e.g., natural organic matter, iron, and nitrate) will absorb energy in the UV wavelengths, thus reducing the transmittance of the water. This reduced transmittance often interferes with the disinfection efficiency of a UV treatment system.

# Appendix F:

Users Handbook

The Users Handbook is a three-ring binder containing copies of the following items:

- Chapter 13 – Daily Operation

- Chapter 15 – Testing the quality of water for microbiological contamination

- Chapter 19 – Reporting Water Quality Test Results

- Chapter 20 – Reporting Problems

- Form 3 – Water Quality Test Results Log

- Form 5 – System History Log

# Appendix G:

UV Dosage Requirements

UV dosage units are µW-sec/cm2

Dosage requirements for 3 log microbe inactivation

| Bacteria | UV Dose | Bacteria | UV Dose |
| --- | --- | --- | --- |
| Agrobacterium lumefaciens 5 | 8,500 | Pseudomonas aeruginosa (Environ.Strain) 1,2,3,4,5,9 | 10,500 |
| Bacillus anthracis 1,4,5,7,9 (anthrax veg.) | 8,700 | Pseudomonas aeruginosa (Lab. Strain) 5,7 | 3,900 |
| Bacillus anthracis Spores (anthrax spores)* | 46,200 | Pseudomonas fluorescens 4,9 | 6,600 |
| Bacillus megatherium Sp. (veg) 4,5,9 | 2,500 | Rhodospirillum rubrum 5 | 6,200 |
| Bacillus megatherium Sp. (spores) 4,9 | 5,200 | Salmonella enteritidis 3,4,5,9 | 7,600 |
| Bacillus paratyphosus 4,9 | 6,100 | Salmonella paratyphi (Enteric Fever) 5,7 | 6,100 |
| Bacillus subtilis 3,4,5,6,9 | 11,000 | Salmonella Species 4,7,9 | 15,200 |
| Bacillus subtilis Spores 2,3,4,6,9 | 22,000 | Salmonella typhimurium 4,5,9 | 15,200 |
| Clostridium tetani | 23,100 | Salmonella typhi (Typhoid Fever) 7 | 7,000 |
| Clostridium botulinum | 11,200 | Salmonella | 10,500 |
| Corynebacterium diphtheriae 1,4,5,7,8,9 | 6,500 | Sarcina lutea 1,4,5,6,9 | 26,400 |
| Dysentery bacilli 3,4,7,9 | 4,200 | Serratia marcescens 1,4,6,9 | 6,160 |
| Eberthella typhosa 1,4,9 | 4,100 | Shigella dysenteriae - Dysentery 1,5,7,9 | 4,200 |
| Escherichia coli 1,2,3,4,9 | 6,600 | Shigella flexneri - Dysentery 5,7 | 3,400 |
| Legionella bozemanii 5 | 3,500 | Shigella paradysenteriae 4,9 | 3,400 |
| Legionella dumoffill 5 | 5,500 | Shigella sonnei 5 | 7,000 |
| Legionella gormanil 5 | 4,900 | Spirillum rubrum 1,4,6,9 | 6,160 |
| Legionella micdadei 5 | 3,100 | Staphylococcus albus 1,6,9 | 5,720 |
| Legionella longbeachae 5 | 2,900 | Staphylococcus aureus 3,4,6,9 | 6,600 |
| Legionella pneumophila (Legionnaire's Disease) | 12,300 | Staphylococcus epidermidis 5,7 | 5,800 |
| Leptospira canicola-Infectious Jaundice 1,9 | 6,000 | Streptococcus faecaila 5,7,8 | 10,000 |
| Leptospira interrogans 1,5,9 | 6,000 | Streptococcus hemolyticus 1,3,4,5,6,9 | 5,500 |
| Micrococcus candidus 4,9 | 12,300 | Streptococcus lactis 1,3,4,5,6 | 8,800 |
| Micrococcus sphaeroides 1,4,6,9 | 15,400 | Streptococcus pyrogenes | 4,200 |
| Mycobacterium tuberculosis 1,3,4,5,7,8,9 | 10,000 | Streptococcus salivarius | 4,200 |
| Neisseria catarrhalis 1,4,5,9 | 8,500 | Streptococcus viridans 3,4,5,9 | 3,800 |
| Phytomonas tumefaciens 1,4,9 | 8,500 | Vibrio comma (Cholera) 3,7 | 6,500 |
| Proteus vulgaris 1,4,5,9 | 6,600 | Vibrio cholerae 1,5,8,9 | 6,500 |
| Molds | UV Dose | Molds | UV Dose |
| Aspergillus amstelodami | 77,000 | Oospora lactis 1,3,4,6,9 | 11,000 |
| Aspergillus flavus 1,4,5,6,9 | 99,000 | Penicillium chrysogenum | 56,000 |
| Aspergillus glaucus 4,5,6,9 | 88,000 | Penicillium digitatum 4,5,6,9 | 88,000 |
| Aspergillus niger (breed mold) 2,3,4,5,6,9 | 330,000 | Penicillium expansum 1,4,5,6,9 | 22,000 |
| Mucor mucedo | 77,000 | Penicillium roqueforti 1,2,3,4,5,6 | 26,400 |
| Mucor racemosus (A & B) 1,3,4,6,9 | 35,200 | Rhizopus nigricans (cheese mold) 3,4,5,6,9 | 220,000 |
| Protozoa | UV Dose | Protozoa | UV Dose |
| Chlorella vulgaris (algae) 1,2,3,4,5,9 | 22,000 | Giardia lamblia (cysts) 3 | 100,000 |
| Blue-green Algae | 420,000 | Nematode Eggs 6 | 40,000 |
| E. hystolytica | 84,000 | Paramecium 1,2,3,4,5,6,9 | 200,000 |
| Virus | UV Dose | Virus | UV Dose |
| Adeno Virus Type III 3 | 4,500 | Influenza 1,2,3,4,5,7,9 | 6,600 |
| Bacteriophage 1,3,4,5,6,9 | 6,600 | Rotavirus 5 | 24,000 |
| Coxsackie | 6,300 | Tobacco Mosaic 2,4,5,6,9 | 440,000 |
| Infectious Hepatitis 1,5,7,9 | 8,000 | 0 | 0 |
| Yeasts | UV Dose | Yeasts | UV Dose |
| Baker's Yeast 1,3,4,5,6,7,9 | 8,800 | Saccharomyces cerevisiae 4,6,9 | 13,200 |
| Brewer's Yeast 1,2,3,4,5,6,9 | 6,600 | Saccharomyces ellipsoideus 4,5,6,9 | 13,200 |
| Common Yeast Cake 1,4,5,6,9 | 13,200 | Saccharomyces sp. 2,3,4,5,6,9 | 17,600 |
| THE INFORMATION CONTAINED IN THIS PUBLICATION IS BASED UPON DATA COLLECTED BY THE ATLANTIC ULTRAVIOLET CORPORATION AND IS BELIEVED TO BE CORRECT. HOWEVER, NO GUARANTEE OR WARRANTY OF ANY KIND, EXPRESSED OR IMPLIED, IS MADE WITH RESPECT TO THE INFORMATION CONTAINED HEREIN. INFORMATION IS SUBJECT TO CHANGE WITHOUT NOTICE. Used by permission of Atlantic Ultraviolet Corporation granted July 26, 2006 |
| 1. "The Use of Ultraviolet Light for Microbial Control", Ultrapure Water, April 1989. 2. William V. Collentro, "Treatment of Water with Ultraviolet Light - Part I", Ultrapure Water, July/August 1986. 3. James E. Cruver, Ph.D., "Spotlight on Ultraviolet Disinfection", Water Technology, June 1984. 4. Dr. Robert W. Legan, "Alternative Disinfection Methods-A Comparison of UV and Ozone", Industrial Water Engineering, Mar/Apr 1982. 5. Unknown 6. Rudolph Nagy, Research Report BL-R-6-1059-3023-1, Westinghouse Electric Corporation. 7. Myron Lupal, "UV Offers Reliable Disinfection", Water Conditioning & Purification, November 1993. 8. John Treij, “Ultraviolet Technology”, Water Conditioning & Purification, December 1995. 9. Bak Srikanth, “The Basic Benefits of Ultraviolet Technology”, Water Conditioning & Purification, December 1995 * Approximate - Various sources may report different inactivation dosages. |

Dosage requirements for Cryptosporidium, Giardia lamblia, and virus 3 log inactivation

(Extracted from LT2ESWTR [See 71 FR 783, Federal Register of 5 Jan 2006])

| Log credit | Cryptosporidium UV dose (µW-sec/cm2) | Giardia lamblia UV dose (µW-sec/cm2) | Virus UV dose (µW-sec/cm2) |
| --- | --- | --- | --- |
| 3.0 | 12,000 | 11,000 | 143,000 |

# Text boxes

Germicidal UV Lamp, 8 watts

Approx 1 liter of water

Flow rate 1 to 3 liters / min

8

9

4

2

10

7

8

5

6

4

1

1

2

9

1

2

10

11

11

4

1

2

7

2

6

6

6

9

2

1

6

6

5

63.0 cm

8.3 cm

13.5 cm

19.0 cm

25.0 cm

41.5 cm

No

2

Yes

STOP

Pre-treat Source Water

Is Iron greater than 0.3

mg/L ?

No

Use Figure 2 to Determine the Maximum Flow Rate

Measure turbidity, iron content and UV irradiance of the source water

Yes

No

STOP

Pre-treat Source Water

UV Irradiance through water less than 400 ?

Yes

STOP

Pre-treat Source Water

Is Turbidity Greater than 5 NTU?

Quartz window

UV Irradiance at Mid-Level