## Slide 1
http://faculty.washington.edu/markbenj/CEE345/
CEE 345, Spring 2012 Part 2: Hydraulics and Open Channel Flow
Instructor: Mark Benjamin, 335 More Hall; 543-7645, markbenj@uw.edu
Text: Munson et al.., Fundamentals of Fluid Mechanics, 6th ed.
Pipe networks, pump selection, hydraulic transients
Flow dependence on depth & slope in rivers, streams, culverts, storm and sanitary sewers
Weekly HW, due beginning of class; no late homework
One lab in HHL; no write-up, but data used in HW
Four Thursday sessions – computer lab, HW, practice problems
Exam on hydraulics on Friday, May 18; open channel questions on final exam

## Slide 2: Our Plan – Weeks 6 and 7
Review energy relationships in single pipes
Extend analysis to progressively more complex systems
  Pipes in parallel or series
  Pipe networks with known flow direction in each pipe
  Interconnected pipe loops and reservoirs where flow direction is not obvious
Consider key factors in selection of pumps to add energy to fluid in a system
Consider some special cases of transients in pipe systems – cavitation and water hammer

## Slide 3: Overview of Pipe Networks
‘Pipe flow’ generally refers to fluid in pipes and appurtenances flowing full and under pressure
Examples: Water distribution in homes, industry, cities; irrigation
System components
  Pipes
  Valves
  Bends
  Pumps and turbines
  Storage (often unpressurized, in reservoirs, tanks, etc.)

## Slide 5: Energy Relationships in Pipe Systems
Energy equation between any two points:
Analysis involves writing expressions for hL in each pipe and for each link between pipes (valves, expansions, contractions), relating velocities based on continuity equation, and solving subject to system constraints (Q, p, or V at specific points).

## Slide 6: Energy Losses in Piping Systems
Darcy-Weisbach equation for headlosses in pipes (major headlosses):

## Slide 7: Estimating f Graphically

## Slide 8
f declines with increasing Re, e.g., increasing V at fixed D.
Trends in f
In turbulent region, for given e/D, f declines more slowly than in laminar region; eventually, the decline stops altogether.
In laminar region, f = 64/Re

## Slide 9: Mathematical Expressions for f
Colebrook and Haaland eqns yield good estimates of f in turbulent flow
Useful for calculations in spreadsheets or special software for pipe flow analysis

## Slide 10: Understanding Headloss in Pipes
Darcy-Weisbach equation:
For travel distance of one pipe diameter ( ):
f is the ratio of energy lost via friction (i.e., shear) to the kinetic energy of the water when the water travels a distance of one pipe diameter

## Slide 11: Example
Compare the velocity and pressure heads for typical conditions in a street main: V = 1.5 m/s; D = 0.5 m; p = 500 kPa
If f = 0.02, hL for each 0.5 m of pipe is 2% of the velocity head, or 0.0023 m, corresponding to 0.0045% of the pressure head.

## Slide 12: Typical Pipe Flow Problems
Type I: Pipe properties (e, D, l) and V known, find hL.
Determine f from Moody diagram or an equivalent equation, and hL from the DW eqn

## Slide 13: Example
A 20-in-diameter galvanized pipe (e = 0.0005 ft) 2 miles long carries 4 cfs at 60oF. Find hL using (a) the Moody diagram and (b) the Colebrook eqn.

## Slide 14
Colebrook eqn:
 | F | G | H
9 | e/D | 0.0003 | 0.0003
10 | Re | 251000 | 2.51E+05
11 | f | 0.03 | 0.03
12 | LHS | =1/SQRT(G11) | 5.774
13 | RHS | =-2*LOG(G9/3.7 + 2.71/G10*G12) | 7.687
14 | LHS - RHS | =G12-G13 | -1.913

## Slide 15
e/D | 0.0003
Re | 2.51E+05
f | 0.017422
LHS | 7.576
RHS | 7.576
LHS - RHS | 2.55E-07

## Slide 16: Typical Pipe Flow Problems
Type II: Pipe properties (e, D, l) and hL known, find V.
Guess V, determine f and hL as in Type I, iterate until hL equals known value, or
Solve Colebrook and DW eqns simultaneously to eliminate V, yielding:

## Slide 17
Solving Type II Pipe Problems: Iterative Approach

## Slide 18
Rearranged D-W eqn:

## Slide 19: Example
For the pipe analyzed in the preceding example, what is the largest flow rate allowable if the total frictional headloss must remain <8 ft?

## Slide 20: Example
For the pipe analyzed in the preceding example, what is the largest flow rate allowable if the total frictional headloss must remain <8 ft?
Substituting known values,

## Slide 21: Typical Pipe Flow Problems
Type III: e, l, V, and hL known, find D.
Several approaches, all iterative; e.g., Guess D, determine V as in Type II, iterate until V equals known value
Example
What diameter galvanized pipe would be required in the preceding examples if a flow rate of 10 cfs was needed, while keeping the total frictional headloss at <8 ft?

## Slide 22
Solving Type III Pipe Problems: Iterative Graphical Approach

## Slide 23
What diameter galvanized pipe would be required in the preceding examples if a flow rate of 10 cfs was needed, while keeping the total frictional headloss at <8 ft?
Solving Type III Pipe Problems: Iterative Analytical Approach

## Slide 24
g | 32.2
hL | 8
l | 10560
eps | 0.0005
nu | 1.22E-05
D_guess | 2
LHS = Q | 10
RHS | 7.72E+00
LHS - RHS | 2.28E+00
g | 32.2
hL | 8
l | 10560
eps | 0.0005
nu | 1.22E-05
D_guess | 2.206594
LHS = Q | 10
RHS | 1.00E+01
LHS - RHS | -8.22E-07

## Slide 25: Dependence of hL on D and V

## Slide 26: Dependence of hL on D and V
In laminar region:
In turbulent region, when f becomes constant:
For a given pipe
For a given pipe
Under typical water distribution conditions, hL in a given pipe can be expressed as kQn with n slightly <2.

## Slide 27: Example
For the systems analyzed in the first two examples, what value of n causes the data to fit the equation hL = kQn?

## Slide 28: Alternative Equations for Flow - Headloss Relationships in Turbulent Pipe Flow
Hazen-Williams equation – widely used for hL as function of flow parameters for turbulent flow at typical velocities in water pipes:
Coefficients shown are for SI units; for BG units, replace 0.849 by 1.318 and 10.7 by 4.73.

## Slide 29: Comparison of Equations for Transitional and Turbulent Curves on the Moody Diagram
 | D-W | H-W* | Manning*
V |  |  | 
Q |  |  | 
hL (=S*l) |  |  | 
*Coefficients shown are for SI units (V in m/s, and D and Rh in m); for BG units (ft/s and ft), replace 0.849 by 1.318; 0.354 by 0.550; 0.278 by 0.432; 10.7 by 4.73; 1/n by 1.49/n; 0.397 by 0.592; 0.312 by 0.465; and 10.3 by 4.66.

## Slide 30: Energy Losses in Bends, Valves, and Other Transitions (‘Minor Losses’)
Minor headlosses generally significant when pipe sections are short (e.g., household, not pipeline)
Caused by turbulence associated with flow transition; therefore, mitigated by modifications that ‘smooth’ flow patterns
Generally much greater for expansions than for contractions
Often expressed as multiple of velocity head:
K is the ratio of energy lost via friction in the device of interest to the kinetic energy of the water (upstream or downstream, depending on geometric details)

## Slide 31: Energy Losses in Contractions
All images from Finemore & Franzini (10e, 2002)

## Slide 32: Energy Losses in Expansions
All images from Finemore & Franzini (10e, 2002)

## Slide 33: Energy Losses in Expansions
All images from Finemore & Franzini (10e, 2002)
Conical diffuser
k’, smooth
k’, rough

## Slide 34: Energy Losses in Pipe Fittings and Bends
All images from Finemore & Franzini (10e, 2002)

## Slide 35: Example
A 5-in-diameter pipe with an estimated f of 0.033 is 110 feet long and connects two reservoirs whose surface elevations differ by 12 feet. The pipe entrance is flushed, and the discharge is submerged.
Compute the flow rate.
How much would the flow rate change if the last 10 ft of the pipe were replaced with a smooth conical diffuser with a cone angle of 10o?

## Slide 37
From graph, for a smooth, 10o cone, kcone = 0.175