## Slide 1: Example. For pump characterized on previous slide, is cavitation a concern if a flow of 3500 gpm of 80oF water is required, and the pump suction is 12 ft above the source reservoir? Headloss in the inlet pipe is given by hL≈6x10-7Q2, with hL in ft and Q in gpm.

## Slide 2
hL,2 = K2Qn
Dz
Pump curve describes how much head the pump will provide at a given Q. Now consider how much head is needed to operate at that Q in a given system (hsys) .
If source and sink are at different elevations, head equal to Dz must be provided, independent of Q.
Frictional headlosses also contribute. These do depend on Q.
hL,1 = K1Qn
z2
z1
z ≡ 0
hL,discharge
hL,valve
hsys = Dz + ShL ≈ Dz + KeqQn

## Slide 3
hsys = Dz + ShL ≈ Dz + KeqQn
hsys
Dz
ShL

## Slide 4
hL,2 =
hL,2 = K2Qn
hL,1 =
hL,1 = K1Qn
z2
z1
z ≡ 0
(hpump is same as TDH; Munson is inconsistent, using ha sometimes for hpump and sometimes for hsys)

## Slide 5
Pump curve (hpump)
System curve (hsys)
z2-z1=hmin
Operating point
For stable operation, the flow rate is such that the pump supplies an amount of head equal to what the system demands.

## Slide 6
hpump or TDH is the total head added by the pump, as expressed by the pump curve (TDH vs. Q). This relationship characterizes the pump, independent of the system in which it is installed.
hsys is the head dissipated due to friction and changes in elevation when fluid passes through the system at a flow rate Q. This relationship characterizes the system, independent of how the flow is generated.
Pump curve (TDH or hpump)
System curve (hsys)
z2-z1=hmin

## Slide 7: Example. A pump curve can be approximated by the equation hpump= 180 - 6.1x10-4Q2, with hL in ft and Q in gpm. If the pump is used to deliver water between two reservoirs via a 4-in-diameter, 600-ft long pipe against a static head of 50 ft, what flow rate will develop, if f=0.02? Ignore minor headlosses.

## Slide 8
Pump curve
System geometry
D-W or H-W

## Slide 9
Changes in system capacity as pipes age
Dependence of system behavior on impeller speed

## Slide 10
Pump and system curves that don’t intersect

## Slide 11
Composite pump curve for identical pumps in series

## Slide 12
Two discharge pipes (and two system configurations) supplied by a single pump
How do the discharge rate and head for the pump relate to the flow rates and heads in the two pipes?

## Slide 13
Composite system curve for two discharge pipes from a single pump

## Slide 14
Composite system curve for two discharge pipes from a single pump

## Slide 15
z2
z1
z ≡ 0
Conventional: Head added by pump equals head lost in rest of system
Modified: Head at some point in system is same based on ‘path’ from either direction
Energy equation is sometimes rearranged to equate a ‘modified’ pump curve with a ‘modified’ system curve
hL,2 = K2Qn
hL,1 = K1Qn

## Slide 16: Similitude and Affinity Laws for Pump Performance
Similitude is useful for extrapolating experimental results to uninvestigated systems
Dimensional analysis allows us to take maximum advantage of similitude relationships by identifying universally valuable parameter combinations
For membrane efficiency: rpart/rpore
For partially full pipe flow: hliq/D
A
B
C

## Slide 17
Procedure: Identify important dependent parameters and make assumptions about independent parameters that control them, i.e.,
Use dimensional analysis to convert these parameters into dimensionless terms, Depi* and Inj*, such that each Depi* term contains only one Depi and one or more Inj. Elimination of dimensions causes the number of Inj* terms to be less than the number of Inj terms; e.g.:

## Slide 18
In hydraulics, similitude typically requires geometric similarity
For pumps, TDH, Pshaft, and h are logical Depi’s; D, li, e, Q, w, r, and m are logical Ij’s, e.g.:
One set of dimensionless groups is:
Head rise coefficient
Power coefficient
Efficiency

## Slide 19
First and second independent parameters are constant for geometrically similar pumps, and fourth is unimportant for high-Re flow (which is typical in pumps). Q/(wD3) is called the flow coefficient, CQ. So:

## Slide 20
CH, CP, and h can be determined for a pump as a function of CQ. Then these relationships will apply to all geometrically similar pumps.
Tentatively select a pump
Obtain CH, CP, and h as fcn of CQ for a geometrically similar pump from manufacturer
Determine CQ for the proposed Q, w, and D in your system
Determine CH and CP for your system
Assess whether anticipated performance is satisfactory; if not, modify w or D to improve performance at given Q
CP
CP
CH
CH
CQ
h
h

## Slide 21
CP
CP
CH
CH
CQ
h
h
A series of homologous pumps is characterized by the following curves. One such pump has an impeller diameter of 0.75 m and operates with maximum efficiency at 1500 rpm (= 25 rps). What is TDH? If the impeller speed is adjusted to 2000 rpm, and a valve is adjusted to maintain the original discharge rate, what will the new efficiency and TDH be?

## Slide 22
CP
CP
CH
CH
CQ
h
h
Under initial conditions (1), h =hmax, so CQ≈ 0.065 and CH≈ 0.19.

## Slide 23
CP
CP
CH
CH
CQ
h
h
After the increase in impeller rotation speed (2), Q and D remain the same, and w increases by 33%, so:
At this value of CQ, h ≈ 62% and CH ≈ 0.21.

## Slide 24
Increasing w by 33% almost doubles TDH.